## Cost Summary
PROPOSED E-BUS MANUFACTURING FACILITY AT SEETHARAMPURAM
COST SUMMARY
S.No. | SUBHEAD DESCRIPTION | AMOUNT (Rs.)
1 | Civil Works | 3218450080
2 | Garden (Landscape works) | 63279150
3 | Furniture | 19065000
4 | Kitchen Equipment | 3907050
5 | HVAC | 13321995
6 | Electrical | 586635691
7 | Plumbing | 25304340
8 | Fire | 127951770
| Total Amount | 4057915076
Note:
1) The rates of all items mentioned above are inculding GST as applicable as on the date of NIT.
2) I/We proprietor / Authorised Signatory of ___________________ having registered office at _____________________________________ willing to execute above works keeping in view tender conditions at (+)/(-) at par _______% on the estimated rates.
Signature of the Contractor
(Name, designation and registered address)

## Civil
NAME OF WORK : CONSTRUCTION AND DEVLOPMENT OF E-VEHICLE MANUFACTURING FACILITY AT SEETHARAMPURAM
SCHEDULE OF ITEMS
CIVIL WORKS
Item No. | DESCRIPTION | UNIT | TOTAL QTY | Rate (Rs) Incl.GST | Amount (in Rs.) Incl.GST
SUBHEAD-I :EARTH WORK & EXCAVATION :
E-1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means in foundation trenches or drains, including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50M
a) | a) All kinds of soils | CUM | 126105 | 118 | 14880390
E-2 | Excavation work by mechanical means (Hydraulic excavator)/ manual means in foundation trenches or drains, including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soils as directed, within a lead of 50 m.
a) | a) Ordinary Rock | CUM | 12744 | 531 | 6767064
b) | b) Hard Rock (Blasting Prohibited) | CUM | 12619 | 590 | 7445210
E-3 | Extra for every additional lift of 1.5 m or part thereof in excavation / banking excavated or stacked materials.
a) | a) All kinds of soils | CUM | 67146.3 | 28 | 1880096.4
E-4 | Filling with available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. | CUM | 81136.3 | 35 | 2839770.5
SUBHEAD-II :ANTI TERMITE TREATMENT :
A-1 | Providing pre constructional anti termtite treatment by injecting Imidacloprid 30.5% SC with 0.075% concentration complete and creating a continuous barrier under and alround the column pits, wall trenches, basement excavation, top surface of plinth filling, junction of wall and floor, along the external perimeter of building, expansion joints, over the top surface of consolidated earth on which apron is to be laid, surroundings of pipes and conduits etc., complete as per specification and stipulations laid down in IS 6313 (Part II). (Plinth area of the building at ground floor level only shall be measured for payment). (To be executed by specialist agency, pest control (India) Ltd. or equivalent approved agency. Guarantee period for 10 years). complete as directed by Engineer-In-Charge.
a) | Imidacloprid 30.5% SC with 0.075% concentration or equivalent as per manufacturer specifications. | Sqm | 168776 | 295 | 49788920
SUBHEAD-III : PLAIN & REINFORCED CEMENT CONCRETE :
C-1 | Providing and laying in position cement concrete M10 grade of specified grade excluding the cost of centering and shuttering - All work up to plinth level :
a) | a) 1:3:6 (1 Cement : 3 coarse sand : 6 graded stone aggregate 10 mm nominal size) | CUM | 20734 | 4683 | 97097322
C-2 | Providing and laying cement concrete M15 Grade in retaining walls, return walls, walls (any thickness) including attached pilasters, columns, piers, abutments, pillars, posts, struts, buttresses, string or lacing courses, parapets, coping, bed blocks, anchor blocks, plain window sills, fillets, sunken floor,etc., up to floor five level, excluding the cost of centering, shuttering and finishing:
a) | a) 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) | CUM | 297 | 5144 | 1527768
C-3 | Making plinth protection 50 mm thick of cement concrete 1:3:6 (1 cement: 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) over 75mm thick bed of dry brick ballast 40 mm nominal size, well rammed and consolidated and grouted with fine sand, including finishing the top smooth. | SQM | 5830 | 725 | 4226750
C-4 | Providing and laying in position machine batched and machine mixed design mix M-30 grade cement concrete for reinforced cement concrete work, using cement content as per approved design mix, including pumping of concrete to site of laying but excluding the cost of centering, shuttering, finishing and reinforcement, including admixtures in recommended proportions as per IS: 9103 to accelerate, retard setting of concrete, improve workability without impairing strength and durability as per direction of Engineer-in-charge. (Note :- Cement content considered in this item is @ 330 kg/cum. Excess/ less cement used as per design mix is payable/recoverable separately).
| a) Foundations, rafts, footings, pedestal, Column, Walls below Finished Floor Level and like | CUM | 28048 | 6232 | 174795136
| b) Columns above Finished Floor Level and like | CUM | 2024 | 6350 | 12852400
| c) Plinth Beams and like | CUM | 967 | 6350 | 6140450
| d) Lintels / Tie Beams, Sloped Beams and like | CUM | 652.9 | 6468 | 4222957.2
| e) Suspended floors / roofs, Sloped roofs, roof of cable /duct trenches and like. | CUM | 5955 | 6468 | 38516940
| f) Chajjas and like | CUM | 56.6 | 6350 | 359410
| g) Staircase waist slabs, landings and steps and like | CUM | 113 | 6468 | 730884
| h)Retaining wall | Cum | 8337 | 6232 | 51956184
C-5 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete
a) | a) Thermo-Mechanically Treated bars (Fe 500 Grade) | MT | 6809.16 | 88500 | 602610660
C-6 | Centering and shuttering including strutting, propping etc. and removal of form for :
a) | Foundations, footings, bases of columns, etc. for mass concrete | SQM | 29409 | 413 | 12145917
b) | Columns, Pillars, Piers, Abutments, Posts and Struts | SQM | 20473 | 531 | 10871163
c) | Lintels, beams, plinth beams, girders, bressumers and cantilevers | SQM | 11582 | 531 | 6150042
d) | Suspended floors, roofs, landings, balconies and access platform | SQM | 31973.16 | 531 | 16977747.96
e) | Weather shade, Chajjas, corbels etc., including edges | SQM | 408.5 | 413 | 168710.5
f) | Stairs, (excluding landings) except spiral-staircases | SQM | 873 | 413 | 360549
g) | Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc. | SQM | 35625 | 413 | 14713125
SUBHEAD-IV : STONE & BRICK MASONRY :
M-1 | Random rubble masonry with hard stone in foundation and plinth including levelling up with cement concrete 1:6:12 (1 cement : 6 coarse sand : 12 graded stone aggregate 20 mm nominal size) upto plinth level with Cement mortar 1:6 (1 cement : 6 coarse sand) | CUM | 12837 | 7729 | 99217173
M-2 | Providing and laying autoclaved aerated cement blocks masonry with 150mm/230mm/300 mm thick AAC blocks in super structure above plinth level up to floor V level with RCC band at sill level and lintel level with approved block laying polymer modified adhesive mortar all complete as per direction of Engineerin- Charge. (The payment of RCC band and reinforcement shall be made for seperately). | CUM | 7329 | 7670 | 56213430
M-3 | Providing and laying autoclaved aerated cement blocks masonry with 100 mm thick AAC blocks in super structure above plinth level up to floor V level in cement mortar 1:4 (1 cement : 4 coarse sand ). The rate includes providing and placing in position 2 Nos 6 mm dia M.S. bars at every third course of masonry work. | CUM | 3202 | 8438 | 27018476
SUBHEAD-V : STEEL & WOOD WORKS :
W-1 | Providing and fixing pressed steel door frames conforming to IS: 4351, manufactured from commercial mild steel sheet of 1.60 mm thickness, including jamb, lock jamb, bead and if required angle threshold of mild steel angle of section 50x25 mm, or base ties of 1.60 mm, pressed mild steel welded or rigidly fixed together by mechanical means, including lock strike plate and shock absorbers as specified and applying a coat of approved steel primer after pre-treatment of the surface as directed by Engineerin-charge:
a) | a) Profile E, fixing with adjustable lugs with split end tail to each jamb | RM | 932 | 544 | 507008
W-2 | Providing and fixing ISI marked flush door shutters conforming to IS : 2202 (Part I) decorative type, core of block board construction with frame of 1st class hard wood and well matched teak 3 ply veneering with vertical grains or cross bands and face veneers on both faces of shutters.
a) | a) 35 mm thick including ISI marked Stainless Steel butt hinges with necessary screws | SQM | 530 | 3279 | 1737870
a) Tower bolts (Al. Anodized)
| i) 200mm long, 10mm dia | Each | 277 | 97 | 26869
b) Aluminum handles
| i) 100mm long | Each | 3 | 58 | 174
| ii) 125mm long | Each | 215 | 65 | 13975
c) Al. Rubber Cleats :
| i) 50mm size | Each | 203 | 90 | 18270
| d) Aluminium anodized floor door stopper of 50mm size of approved design and make. | Each | 179 | 39 | 6981
| e) Aluminum Aldrop 300mm long with 16mm dia rod | Each | 227 | 277 | 62879
W-3 | Providing and fixing aluminium extruded section body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 36 kg to 80 kg and door width from 701 mm to 1000 mm), with double speed adjustment with necessary accessories and screws etc. complete. | Each | 100 | 911 | 91100
W-4 | Providing and fixing Fiber Glass Reinforced plastic (FRP) Door Frames of cross-section 90 mm x 45 mm having single rebate of 32 mm x 15 mm to receive shutter of 30 mm thickness. The laminate shall be moulded with fire resistant grade unsaturated polyester resin and chopped mat. Door frame laminate shall be 2 mm thick and shall be filled with suitable wooden block in all the three legs. The frame shall be covered with fiber glass from all sides. M.S. stay shall be provided at the bottom to steady the frame. | RM | 871 | 747 | 650637
W-5 | Providing and fixing to existing door frames, 30 mm thick Glass Fibre Reinforced Plastic (FRP) panelled door shutter of required colour and approved brand and manufacture, made with fire - retardant grade unsaturated polyester resin, moulded to 3 mm thick FRP laminate for forming hollow rails and styles, with wooden frame and suitable blocks of seasoned wood inside at required places for fixing of fittings, cast monolithically with 5 mm thick FRP laminate for panels conforming to IS: 14856, including fixing to frames. | SQM | 312 | 3715 | 1159080
W-6 | Providing, supplying & fixing of glazed 3 Track -2 Panel Sliding Window with White profile made out of multi chambered uPVC sections with TPV gaskets having isolated drainage and reinforced with Galvanized Iron profiles through out the window. The outer frame having an overall size of 108 x 45 mm with reinforcement of 1 mm thickness and sash with overall size of 39 x 65 mm with reinforcement of 1.5 mm thickness, mesh sash of overall size 37 x 58mm reinforced with 1.2 mm of GI 120 GSM. Glazing bead for fixing of glass shall be of size 20 x 18mm and coextruded with gasket. Stainless steel (S.S) mesh shall be provided in mesh shutter Windows shall be provided with 6mm plain Toughened glass, standard hardware & single point locking system of flush lock. Wall thickness of frame & sash shall be 2 - 2.2 mm. | SQM | 2749 | 6983 | 19196267
W-7 | Providing, supplying & fixing of glazed Louvers + Ex.Fan Provision made out of multi chambered uPVC sections with TPV gaskets having isolated drainage and reinforced with Galvanized Iron profiles through out the window. The outer frame having a overall size of 60 x 55 mm with reinforcement of 1 mm thickness and mullion with overall size of 60 x 74mm with reinforcement of 1mm thickness. Glazing bead for fixing of glass shall be of size 20 x 34 mm and coextruded with gasket. Composition of profile shall consist a minimum of 6 PHR of TiO₂ for every 100 parts of PVC resin. Ventilator shall be provided with 4mm PINHEAD Louvers, standard hardware. Wall thickness of frame & sash shall be 2.2 - 2.4 mm. | SQM | 816.6 | 3540 | 2890764
W-8 | Providing and fixing M.S. grills of required pattern in frames of windows etc., with M.S. flats, square or round bars etc. including priming coat with approved steel primer all complete. | Kg | 13063 | 142 | 1854946
W-9 | Supplying and providing motorized electrically operated rolling shutters of size 5.00m x 6.00m conforming to the specifications given below: Double skin with PUF insulation, curtain made of double skinned galvanised steel laths, pressed galvalume steel hood & motor cover, finish (Rolling shutter color) - Polyurethane spray painted to RAL 1023 (Traffic Yellow) over one coat of epoxy primer, Three station push button with deadman control operation & CE Certified CRS Compact Gear P.R.C. Make Indirect Drive Operator. Shutter must also have seals at lintel level, Bottom seal made up of EPDM Profile. IP 65 Compliant | SQM | 4505 | 2950 | 13289750
W-10 | Structural Glazing
a | Providing and supplying aluminium extruded tubular and other aluminium sections as per the architectural drawings and approved shop drawings , the aluminium quality as per grade 6063 T5 or T6 as per BS 1474,including super durable powder coating of 60-80 microns conforming to AAMA 2604 of required colour and shade as approved by the Engineer-in-Charge. ( The item includes cost of material such as cleats, sleeves, screws etc. necessary for fabrication of extruded aluminium frame work. Nothing extra shall be paid on this account). The weight of aluminium extruded section shall be taken for purpose of payment. | Kgs | 16110 | 413 | 6653430
b | Designing, fabricating, testing, protection, installing and fixing in position semi (grid) unitized system of structural glazing (with open joints) for linear as well as curvilinear portions of the building for all heights and all levels, including: | SQM | 1074 | 3422 | 3675228
Structural analysis & design and preparation of shop drawings for the specified design loads conforming to IS 875 part III (the system must passed the proof test at 1.5 times design wind pressure without any failure), including functional design of the aluminum sections for fixing glazing panels of various thicknesses, aluminium cleats, sleeves and splice plates etc. gaskets, screws, toggles, nuts, bolts, clamps etc., structural and weather silicone sealants, flashings, fire stop (barrier)-cum-smoke seals, microwave cured EPDM gaskets for water tightness, pressure equalisation & drainage and protection against fire hazard including:
Fabricating and supplying serrated M.S. hot dip galvanised / Aluminium alloy of 6005 T5 brackets of required sizes, sections and profiles etc. to accommodate 3 Dimentional movement for achieving perfect verticality and fixing structural glazing system rigidly to the RCC/ masonry/structural steel framework of building structure using stainless steel anchor fasteners/ bolts, nylon seperator to prevent bimetallic contacts with nuts and washers etc. of stainless steel grade 316, of the required capacity and in required numbers.
Providing and filling, two part pump filled, structural silicone sealant and one part weather silicone sealant compatible with the structural silicone sealant of required bite size in a clean and controlled factory / work shop environment, including double sided spacer tape, setting blocks and backer rod, all of approved grade, brand and manufacture, as per the approved sealant design, within and all around the perimeter for holding glass.
Providing and fixing in position flashings of solid aluminium sheet 1 mm thick and of sizes, shapes and profiles, as required as per the site conditions, to seal the gap between the building structure and all its interfaces with curtain glazing to make it watertight.
Making provision for drainage of moisture/ water that enters the curtain glazing system to make it watertight, by incorporating principles of pressure equalization, providing suitable gutter profiles at bottom (if required), making necessary holes of required sizes and of required numbers etc. complete. This item includes cost of all inputs of designing, labour for fabricating and installation of aluminium grid, installation of glazed units, T&P, scaffolding and other incidental charges including wastages etc., enabling temporary structures and services, cranes or cradles etc. as described above and as specified. The item includes the cost of getting all the structural and functional design including shop drawings checked by a structural designer, dully approved by Engineer-in-charge. The item also includes the cost of all mock ups at site, cost of all samples of the individual components for testing in an approved laboratory, field tests on the assembled working structural glazing as specified, cleaning and protection till the handing over of the building for occupation. In the end, the Contractor shall provide a water tight structural glazing having all the performance characteristics etc. all complete as required, as per the Architectural drawings, as per item description, as specified, as per the approved shop drawings and as directed by the Engineer- in-Charge.
W-11 | Designing, fabricating, testing, installing and fixing in position Curtain Wall with Aluminium Composite Panel Cladding, with open grooves for linear as well as curvilinear portions of the building , for all heights and all levels etc. including: | Sqm | 2160 | 4130 | 8920800
(a) Structural analysis & design and preparation of shop drawings for pressure equalisation or rain screen principle as required, proper drainage of water to make it watertight including checking of all the structural and functional design.
(b) Providing, fabricating and supplying and fixing panels of aluminium composite panel cladding in pan shape in metalic colour of approved shades made out of 4mm thick aluminium composite panel material consisting of 3mm thick FR grade mineral core sandwiched between two Aluminium sheets (each 0.5mm thick). The aluminium composite panel cladding sheet shall be coil coated, with Kynar 500 based PVDF / Lumiflon based fluoropolymer resin coating of approved colour and shade on face # 1 and polymer (Service) coating on face # 2 as specified using stainless steel screws, nuts, bolts, washers, cleats, weather silicone sealant, backer rods etc.
(c) The fastening brackets of Aluminium alloy 6005 T5 / MS with Hot Dip Galvanised with serrations and serrated washers to arrest the wind load movement, fasteners, SS 316 Pins and anchor bolts of approved make in SS 316, Nylon separators to prevent bi-metallic contacts all complete required to perform as per specification and drawing The item includes cost of all material & labour component, the cost of all mock ups at site, cost of all samples of the individual components for testing in an approved laboratory, field tests on the assembled working curtain wall with aluminium composite panel cladding, cleaning and protection of the curtain wall with aluminium composite panel cladding till the handing over of the building for occupation. Base frame work for ACP cladding is payable under the relevant aluminium item.s The Contractor shall provide curtain wall with aluminium composite panel cladding, having all the performance characteristics all complete , as per the Architectural drawings, as per item description, as specified, as per the approved shop drawings and as directed by the Engineer-in-Charge. However, for the purpose of payment, only the actual area on the external face of the curtain wall with Aluminum Composite Panel Cladding (including width of groove) shall be measured in sqm. up to two decimal places. Location : East and South Side Elevation
W-12 | Providing and fixing stainless steel ( Grade 304) railing made of Hollow tubes, channels, plates etc., including welding, grinding, buffing, polishing and making curvature (wherever required) and fitting the same with necessary stainless steel nuts and bolts complete, i/c fixing the railing with necessary accessories & stainless steel dash fasteners , stainless steel bolts etc., of required size, on the top of the floor or the side of waist slab with suitable arrangement as per approval of Engineer-in charge, (for payment purpose only weight of stainless steel members shall be considered excluding fixing accessories such as nuts, bolts, fasteners etc.). | Kg | 7216 | 472 | 3405952
W-13 | Fencing with angle iron post placed at required distance embedded in cement concrete blocks, every 15th post, last but one end post and corner post shall be strutted on both sides and end post on one side only and provided with horizontal lines and two diagonals interwoven with horizontal wires, of barbed wire weighing 9.38 kg per 100 m (minimum), between the two posts fitted and fixed with G.I. staples, turn buckles etc. complete. (Cost of posts, struts, earth work and concrete work to be paid for separately). Payment to be made per metre cost of total length of barbed wire used. | Kg | 12960 | 106 | 1373760
W-14 | Fencing with angle iron post placed at required distance embedded in cement concrete blocks, every 15th post, last but one end post and corner post shall be strutted on both sides and end post on one side only and provided with horizontal lines and two diagonals interwoven with horizontal wires, of barbed wire weighing 9.38 kg per 100 m (minimum), between the two posts fitted and fixed with G.I. staples, turn buckles etc. complete. (Cost of posts, struts, earth work and concrete work to be paid for separately). Payment to be made per metre cost of total length of barbed wire used.
| With G.I. barbed wire | Rmt | 25196 | 21 | 529116
W-15 | Providing orange colour safety foot rest of minimum 6 mm thick plastic encapsulated as per IS : 10910, on 12 mm dia steel bar conforming to IS: 1786, having minimum cross section as 23 mmx25 mm and over all minimum length 263 mm and width as 165 mm withminimum 112 mm space between protruded legs having 2 mm tread on top surface by ribbing or chequering besides necessary and adequate anchoring projections on tail length on 138 mm as per standard drawing and suitable to with stand the bend test and chemical resistance test as per specifications and having manufacture's permanent identification mark to be visible even after fixing, including fixing in manholes with 30x20x15 cm cement concrete block 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) complete as per design. | Nos | 160 | 623 | 99680
SUBHEAD-VI : FLOORING :
F-1 | Supplying and applying primer, epoxy 17 @ 0.2 kg/ Sqm, then an underalay of 2 mm underlay screed with Resin & Hardener using Cipoxy 17 & FQ Sand 200 (Total Consumption of resin and hardener will be 0.9 kg/ Sqm and consumption of FQ Sand 200 will be 2 kg/ Sqm) and Finally the Top Coat with epoxy self levelling topping of 1 mm using Floortop 1000 with colorant for topping. | SQM | 9600 | 767 | 7363200
F-2 | Providing and laying 150mm thick C.C. flooring of mix M-20 with ready mixed concrete from batching plant. The ready mixed concrete shall be laid and finished with screed board vibrator, vacuum dewatering process and finally finished by floating, brooming with wire brush etc. including panel shuttering with panels of size 3m x 4m but excluding reinforcement steel all complete as per specifications and directions of Engineer-incharge. | CUM | 198 | 6100 | 1207800
F-3 | Providing and laying flamed finish Granite stone flooring in required design and patterns, in linear as well as curvilinear portions of the building all complete as per the architectural drawings with 18 mm thick stone slab over 20 mm (average) thick base of cement mortar 1:4 (1 cement : 4 coarse sand) laid and jointed with cement slurry and pointing with white cement slurry admixed with pigment of matching shade including rubbing, curing and polishing etc. all complete as specified and as directed by the Engineer-in-Charge : | SQM | 733 | 5900 | 4324700
F-4 | 52 mm thick cement concrete flooring with concrete hardener topping, under layer 40 mm thick cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) and top layer 12 mm thick cement hardener consisting of mix 1:2 (1 cement hardener mix : 2 graded stone aggregate 6 mm nominal size) by volume, hardening compound mixed @ 2 litre per 50 kg of cement or as per manufacturer’s specifications. This includes cost of cement slurry, but excluding the cost of nosing of steps etc., complete. | SQM | 724 | 910 | 658840
F-5 | Cement skirting 150mm high in CM (1:3) 18mm thick finished with a floating coat of neat cement etc., complete. | SQM | 65 | 607 | 39455
F-6 | Providing and laying Ceramic glazed floor tiles of size of thickness upto 10mm and 300x300 mm of 1st quality conforming to IS : 15622 of approved make in colours such as White, Ivory, Grey, Fume Red Brown, laid on 20 mm thick cement mortar 1:4 (1 Cement : 4 Coarse sand), including pointing the joints with white cement and matching pigment etc., complete all as directed by Engineer - in - Charge. | SQM | 1586 | 472 | 748592
F-7 | Providing and fixing Ist quality ceramic glazed wall tiles conforming to IS: 15622 (thickness to be specified by the manufacturer), of approved make, in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete. | SQM | 3861.4 | 767 | 2961693.8
F-8 | Providing and laying vitrified floor tiles of size 600x600 mm (thickness to be specified by the manufacturer) with water absorption less than 0.08% and conforming to IS : 15622, of approved make, in all colours and shades, laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand), including grouting the joints with white cement and matching pigments etc., complete. |  |  |  | 0
a | Size of Tile 600x600 mm | SQM | 9841 | 708 | 6967428
b | Size of Tile 1000x1000 mm | SQM | 1417 | 708 | 1003236
F-9 | Providing and laying Vitrified tiles of size 600x600 mm (thickness to be specified by manufacturer), with water absorption less than 0.08 % and conforming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete. | SQM | 540 | 885 | 477900
F-10 | Stone work (machine cut edges Veneer work) for wall lining upto 10 m height, backing filled with a grout of 12 mm thick cement mortar 1:3 (1 Cement : 3 coarse sand) and jointed with Cement mortar 1:2 (1 cement: 2 stone dust), including rubbing and polishing complete. (To be secured to the backing and the sides by means of cramps and pins which shall be paid for separately).
| Kota stone slabs exposed face dressed and rubbed. | Sqm | 515 | 2596 | 1336940
F-11 | Providing and laying C.C. pavement of mix M-25 with ready mixed concrete from batching plant. The ready mixed concrete shall be laid and finished with screed board vibrator , vacuum dewatering process and finally finished by floating, brooming with wire brush etc. complete as per specifications and directions of Engineer-incharge. (The panel shuttering work shall be paid for separately)(Note:- Cement content considered in this item is @ 330 kg/cum. Excess/less cement used as per design mix is payable/ recoverable separately). | Cum | 24138 | 6100 | 147241800
F-12 | Providing mixing and laying The areas indicated shall be applied with an epoxy resin based static Conductive floor topping, which shall provide an effective charge dissipation to the earth when applied over concrete or steel substrates. static Conductive areas (Resistance 25x10^3 to 1 x10^6 Ohms) When measured for surface resistance in accordance with ASTM F150, the static Conductive topping including Under coat shall be in the range of 25 x 10^3 - 1 x 10^6 Ohms. The surface resistance of the Conductive undercoat shall be in the range of 3 x 10^3 - 9 x 10^3 Ohms. shall have the following property CS (BS 6319) 50N/mm2, TS: 16N/mm2, FS: 34N/mm2 SELF ADHESIVE COPPER TAPE of 3M 1181, of 100microns thickness and 25mm in width shall be positioned in appropriate grid form, well connected to a minimum two Earthing point in a room, ensure that no point on the floor is at a distance of more than 6m from a copper tape. It is available in a range of standard colours. Cost Inclusive of Supply, apply, equipment. Exclusive of Taxes as applicable. Client shall provide Storage, Power, water, etc. Flooring work shall be executed by manufacturer authorised Applicator. | Sqm | 352 | 531 | 186912
SUBHEAD-VII : PLASTERING & SURFACE TREATMENT :
FN-1 | 6 mm thick plastering in cement mortar 1:3 (1 cement: 3 fine sand) at all levels and locations for all concrete surfaces of columns, beams and slabs finished smooth and even, etc., complete all as directed by Engineer - in - Charge. | SQM | 14203 | 330 | 4686990
FN-2 | 15 mm thick plastering, in cement mortar 1:3 (1 cement :3 fine sand) finished neat with extra cement including benching etc. all as directed by Engineer - in - Charge. | SQM | 87053.81 | 413 | 35953223.53
FN-3 | 18 mm thick sand faced cement plastering on external surfaces of brick or concrete surfaces in two layers consisting of 6 mm thick cement mortar 1:3 (1 cement :3 fine sand) top coat mixed with integral water proofing compound over a base coat 12 mm thick cement mortar 1:5 (1 cement :5 coarse sand), finished sand face including providing and fixing 12mmx22mm gauge chicken mesh with all necessary hardware at the junction of RCC and brick work with overlapping of 100 mm on both sides, etc., complete at all levels and locations and as directed by Engineer - in - Charge. | SQM | 42095 | 472 | 19868840
FN-4 | White washing with lime on new walls and ceilings three coats to give an even shade including preparation of surfaces etc.,complete all as directed by Engineer - in - Charge. | SQM | 31772 | 24 | 762528
FN-5 | Providing and applying plaster of Paris putty of 2 mm thickness over plastered surface to prepare the surface even and smooth and applying 2 coats of oil bound distemper of approved brand and manufacture to give an even shade on new work of two or more coats over and including priming coat, etc., complete all as directed by Engineer - in - Charge. | SQM | 54593.81 | 118 | 6442069.58
FN-6 | Providing and Finishing walls with textured exterior paint of required shade on new work (Two or more coats applied @ 3.28 ltr/10 sqm) over and including priming coat of exterior primer applied @ 2.20kg/ 10 sqm | SQM | 24088 | 212 | 5106656
FN-7 | Providing and applying two coats of synthetic enamel paint of approved brand and shade over a coat of primer including preparation of surface and applying approved brand putty on following surfaces at all levels and locations etc., complete all as directed by Engineer - in - Charge:
| a) Steel surfaces with zinc chromate primer | SQM | 1205 | 199 | 239795
| b) Wooden surface with approved primer | SQM | 33 | 205 | 6765
SUBHEAD- VIII: FALSE CEILING
ST-1 | Providing and fixing tiled false ceiling of specified materials of size 595x595 mm in true horizontal level, suspended on inter locking metal grid of hot dipped galvanized steel sections ( galvanized @ 120 grams/ sqm, both side inclusive) consisting of main "T" runner with suitably spaced joints to get required length and of size 24x38 mm made from 0.30 mm thick (minimum) sheet, spaced at 1200 mm center to center and cross "T" of size 24x25 mm made of 0.30 mm thick (minimum) sheet, 1200 mm long spaced between main "T" at 600 mm center to center to form a grid of 1200x600 mm and secondary cross "T" of length 600 mm and size 24x25 mm made of 0.30 mm thick (minimum) sheet to be interlocked at middle of the 1200x600 mm panel to form grids of 600x600 mm and wall angle of size 24x24x0.3 mm and laying false ceiling tiles of approved texture in the grid including, required cutting/making, opening for services like diffusers, grills, light fittings, fixtures, smoke detectors etc. Main "T" runners to be suspended from ceiling using GI slotted cleats of size 27 x 37 x 25 x1.6 mm fixed to ceiling with 12.5 mm dia and 50 mm long dash fasteners, 4 mm GI adjustable rods with galvanised butterfly level clips of size 85 x 30 x 0.8 mm spaced at 1200 mm center to center along main T, bottom exposed width of 24 mm of all T-sections shall be pre-painted with polyester paint, all complete for all heights as per specifications, drawings and as directed by Engineer-in-charge.
| 12.5 mm thick fully Perforated Gypsum Board tile made from plasterboard having glass fibre conforming to IS: 2095 part I, of size 595x595 mm, having perforation of 9.7x9.7 mm at 19.4 mm c/c with center borders of 48 mm and the side borders of 30 mm, backed with non woven tissue on the back side, having an NRC ( Noise Reduction Coefficient) of 0.79, with 50 mm resin bonded glass wool backing. | SQM | 4454 | 889 | 3959606
SUBHEAD- IX: MISCELLANEOUS
RAIN WATER SPOUT AND PIPE
MIS-1 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion, including providing and fixing unplasticised -PVC pipe clips of approved design to unplasticised - PVC rain water pipes by means of 50x50x50 mm hard wood plugs, screwed with M.S. screws of required length, including cutting brick work and fixing in cement mortar 1:4 (1 cement : 4 coarse sand) and making good the wall etc. complete.
a) | Single socketed pipes of 110mm diameter | RM | 6252 | 295 | 1844340
SUBHEAD-X : Waterproofing
Terrace Waterproofing
WP-1 | Surface Preparation: RCC Surfaces must be clean, even and sound concrete. Remove all oil, dirt, laitance and other Contaminants by manually. Grout: Providing Chemical injection treatment in the form of pressure grouting to the cold joint by injecting cement slurry mixed with grout admixture ArmGrout Additive @ 250 gms per bag of cement, in the required consistency through the pre fixed PVC nozzles in the 10mm dia holes, fixing of PVC nozzles with quick setting compound ReArm Fix 10S and final cutting the projected nozzles and sealing off the PVC nozzles after the injection operation is over with quick setting compound ReArm Fix 10S, non-shrink rapid setting mortar compound, finishing, curing etc. as per manufacturers specification and as directed. (cement has to be supplied by the main contractor). Application of Primer: Apply FloArm primer 1260 over well prepared surface. Application of Hybrid Polyurea waterproof coating: Application of Polyurethane waterproof coating of two component, spray applied fast setting coating based out of modified polyurethane/ Hybrid Polyurea Hybrid to achieve an elastic, high crack bridging waterproofing coating with long life expectancy waterproofing system AquaArm Purtech H 1 manufactured and supplied by MYK Arment or equivalent. AquaArm Purtech H1 can be applied at 1Kg/Sqm/mm thickness. The membrane will have the following technical parameters: Elongation : >500 % Recovery from 100 % Elongation : >85% Tensile Strength : >12 N/mm2 | Sqm | 8002 | 1121 | 8970242
WP-2 | Waterproofing Treatment to Retaining Wall
a | Surface Preparation: (after de shuttering & curing) RCC Surfaces must be clean, even and sound concrete. Remove all oil, dirt, laitance and other Contaminants by manually. Construction joint treatment: Starter level lift joint, pour joints or critical joints in the wall make a “V” groove with 20mmx20mm width and depth. Fix the PVC Pipe of 10mm dia into the drilled hole and pack it tightly use quick setting cement - ReArmFix 10S. Packing the groove with non-shrink grout ArmGrout M65 Inject cementitious slurry by adding cement grout ArmGrout Additive maintaining W/P ratio of 0.45 with the dosage of 250gms/bag of cement under pressure through the nozzles. This should be applied before application of crystalline coating of AquaArm IC. Providing and applying crystlline waterproofing treatment to RCC retaining wall. The waterproofing to be carried out using AquaArm IC of MYK Arment make, by preparing AquaArm IC slurry, by adding 6.75 to 8 liter clean water per 25 kg of AquaArm IC. Both the components should be mixed with a mechanical stirrer (300 to 700 RPM) until a lump free, homogeneous slurry is obtained. The slurry should be applied with a brush @ 1.5 kg/Sqm in two coats on the concrete substrate. The second coat should be applied when the first coat is still tacky. | Sqm | 1267 | 531 | 672777
WP-3 | Toilets
| Surface Preparation: RCC Surfaces must be clean, even and sound concrete. Remove all oil, dirt, laitance and other Contaminants by manually. Grout: Providing Chemical injection treatment in the form of pressure grouting to the cold joint by injecting cement slurry mixed with grout admixture ArmGrout Additive @ 250 gms per bag of cement, in the required consistency through the pre fixed PVC nozzles in the 10mm dia holes, fixing of PVC nozzles with quick setting compound ReArm Fix 10S and final cutting the projected nozzles and sealing off the PVC nozzles after the injection operation is over with quick setting compound ReArm Fix 10S, non-shrink rapid setting mortar compound, finishing, curing etc. as per manufacturers specification and as directed. (cement has to be supplied by the main contractor), Waterproofing application: - Waterproofing application:- Providing and application of single component synthetic rubber based polymer dispersion which dries to form a seamless elastomeric waterproof membrane AquaArm Saniflex at a coverage of 1.2 kg /m2 over a primed surface with AquaArm UniPrimer-GE. The coating shall be carried out upto 300mm at wall areas. | Sqm | 3065.2 | 531 | 1627621.2
WP-4 | Bore Packing :- All the pipes to placed / inserted in the core cut areas, shall be rough with sand paper and apply a coat of bonding agent with ReArm SBR 45, around the cut bores. Grouting the gaps between the pipe and the core cutting by an expansive cementitious grout ArmGrout M-65 that shall be poured into the gaps after fixing in place an effective leak-free shuttering.
a | 75mm Dia | Nos | 183 | 415 | 75945
b | 125mm Dia | Nos | 166 | 485 | 80510
c | 160mm Dia | Nos | 135 | 555 | 74925
SUBHEAD- VIII : Roads
RD-1 | Preparation and consolidation of sub grade with power road roller of 8 to 12 tonne capacity after excavating earth to an average of 22.5 cm depth, dressing to camber and consolidating with road roller including making good the undulations etc. and re-rolling the sub grade and disposal of surplus earthwith lead upto 50 metres. | Sqm | 115260 | 130 | 14983800
RD-2 | Banking excavated earth in layers not exceeding 20 cm in depth, breaking clods, watering, rolling each layer with ½ tonne roller, or wooden or steel rammers, and rolling every 3rd and top-most layer with power roller of minimum 8 tonnes and dressing up, in embankments for roads, flood banks, marginal banks, and guide banks etc., lead upto 50 m and lift upto 1.5 m in all kinds of soils. | Cum | 44240 | 413 | 18271120
RD-3 | Providing, laying, spreading and compacting graded stone aggregate (size range 53 mm to 0.075 mm ) to wet mix macadam (WMM) specification including premixing the material with water at OMC in for all leads & lifts, laying in uniform layers with mechanical paverfinisher in sub- base / base course on well prepared surface and compacting with vibratory roller of 8 to 10 tonne capacity to achievethe desired density, complete as per specifications and directions of Engineer-in-Charge. | Cum | 24257 | 2124 | 51521868
RD-4 | Cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 40 mm nominal size) in pavements, laid to required slope and camber in panels as required including consolidation finishing and tamping complete. | Sqm | 15954 | 5144 | 82067376
RD-5 | Providing and laying design mix cement concrete of M-30 grade, in roads/ taxi tracks/ runways, using cement content as per design mix, using coarse sand and graded stone aggregate of 40 mm nominal size in appropriate proportions as per approved & specified design criteria, providing dowel bars with sleeve/ tie bars wherever required, laying at site, spreading and compacting mechanically by using needle and surface vibrators, levelling to required slope/ camber, finishing with required texture, including steel form work with sturdy M.S. channel sections, curing, making provision for contraction/expansion, construction & longitudinal joints (10 mm wide x 50 mm deep) by groove cutting machine, providing and filling joints with approved joint filler and sealants, complete all as per direction of Engineer-in-charge (Item of joint fillers, sealants, dowel bars with sleeve/ tie bars to be paid separately).
a | Cement concrete prepared with batch mixing machine | Cum | 15954 | 6232 | 99425328
RD-6 | Providing and laying at or near ground level factory made kerb stone of M-25 grade cement concrete in position to the required line, level and curvature, jointed with cement mortar 1:3 (1 cement: 3 coarse sand), including making joints with or without grooves (thickness of joints except at sharp curve shall not to more than 5mm), including making drainage opening wherever required complete etc. as per direction of Engineer-in-charge (length of finished kerb edging shall be measured for payment). (Precast C.C. kerb stone shall be approved by Engineer-in-charge). | Cum | 1434 | 6099 | 8745966
RD-7 | Providing and laying 80mm thick faciory made cement concrete interlocking paver block of M -30 grade made by block makingmachine with strong vibratory compaction, of approved size, design & shape, laid in required colour and pattern over and including 50mm thick compacted bed of coarse sand, filling the joints with line sand etc. all complete as per the direction of Engineer-in-charge. | Sqm | 50081 | 684 | 34255404
RD-8 | Dry stone pitching 22.5 cm thick laid in courses and required profile with hammer dressed stones having no side less than 15 cm, with minimum depth of 20 cm including preparing the bedding surface etc. all complete. | Sqm | 3360 | 413 | 1387680
RD-9 | Providing and laying non-pressure NP2 class (light duty) R.C.C. pipes with collars jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 fine sand) including testing of joints etc., complete.
a | 150 mm dia. R.C.C. pipe | Rmt | 1330 | 525 | 698250
b | 300 mm dia. R.C.C. pipe | Rmt | 80 | 959 | 76720
c | 450 mm dia. R.C.C. pipe | Rmt | 269 | 1574 | 423406
d | 2000 mm dia. R.C.C. pipe | Rmt | 320 | 7434 | 2378880
RD-10 | Supply & Design of Tensile Membrane & Supporting Structure, Supply of Serge Ferrari Fabric, Fabrication of Membrane and connection systems, support MS structure, Installation of structural Membrane including fabric flashing and Connection system & tensioning and Painting the structure with One coat of Primer and Two coats of Enamel brush paint | Sqm | 11429 | 4130 | 47201770
SUBHEAD- I : Area Development
AD-1 | Excavating, supplying and filling of local earth (including royalty) by mechanical transport upto a lead of 2km also including ramming and watering of the earth in layers not exceeding 20 cm in trenches, plinth, sides of foundation etc. complete. | Cum | 450000 | 118 | 53100000
SUBHEAD-XI : PEB Structures
PEB-1 | Design, Manufacture at factory, Fabrication, inspection, testing and supply of all required materials and on site erection of PEB structural syatem in accordance and in compliance with the all necessary codes, Structural DBR shared, as per general specifications for the required system, standard product specifications. The design of the PEB structural system is subject to proof check by third party. Modification if any to the design as a result of the proof check have to be carried out at no extra cost. | L/S | 9500 | 119180 | 1132210000
Basic Building Description: Frame Type (Ridged frame with Inteermediate Columns) Clear height (m) : As per Architectural designs Roof Slope 1:20 Type of End Frames - Rigid Frame Wind Bracing - Portal Roof Cladding - Standing seam roofing system Eave Condition - Curved eave (With necessary Supporting Framework) Wall Sheeting - 0.50mm TCT Steel Work Finish : Frames , Built-Up / HR sections + Zinc Chromite with SA2.5 + Two coats of Epoxy finish paint of Approved shade. Bracings + Zinc Chromite with SA2.5 + Two coats of Epoxy finish paint of Approved shade. Primary Members : Primary structural framing shall include transverse/ rigid frames / lean - to - rafters and columns. Secondary Members : 275 GSM Secondary structural framing shall include purlins, girts, eave struts, wind bracing, flange bracing, base angles, clips/ cleats and required miscellaneous structural parts. Connections : All field connections shall be bolted (unless otherwise noted). Primary bolted connections shall be furnished with high strength bolts confirming to physical specifications of ASTM A325 (or equivalent). Secondary bolted connections shall be furnished with machine bolts confirming to the physical specification of ASTM A 307(or equivalent). Physical Specifications of Structural Members: Members fabricated from plate or bar stock shall have flanges and webs joined on one side of the web b a continuous welding process and will confirm to the physical specifications of ASTM A570 (grade 50)or equivalent and shall have a minimum yield strength of 50,000 P.S.I (345 MPa). Members fabricated by cold forming processes shall confirm to the physical specificatios of ASTM A570 (grade 50) or equivalent and have a minium yield strength of 50,000 P.S.I (345 MPa). Roof and wall cladding with 0.60mm TCT sheet shall confirm to the physical specifications of ASTM A792M coating AZ150 (Grade 50) or equivalent and have a minium yield strength of 50,000 P.S.I (345 MPa). All other secondary members shall have a minium yield strength of 36,000 P.S.I (250 MPa). Sheeting Fastners: Standard fastners shall be No.14, Type self tapping sheet metal screws with metal and neoprene washers. All screws shall have hexagonal heads, be color coated to match roof and wall sheeting and made of zinc palted steel. Sealer/Rope Seal: This shall be applied at all side laps and end of roof panels and around self-flashing windows. Sealer shall be 6mm wide x 5 mm thick asbestos fibre filled, pressure- sensitive butyl tape. The sealer be non asphaltic, nonshrinking non dryig and toxic and shall have goof adhesion to metals, plastics and painted surfaces at temperature from-51 deg. 'C' to +104 deg. 'C'. Flashing and Trim: Flashing and/ or trim shall be furnished at the rake, corners, eaves, frames openings, rain water down take pipes and wherever necessary to provede weather-tightness and finished appearance. Complete as directed by Engineer-in-charge Materials shall be 26G thick, confirming to the physical specifications of ASTM A 446 Grade C or Equvalent and shall have minium yield strength of 40,000 P.S.I. (275 Mpa). Valley gutter to be of GI - 2mm thick. All downtake pipes to be of PVC and not FRP based. All down take pipes to be taken atleast 300mm into the drains and not left over the drains/chambers. Torque wrench testing of bolts with digital torque wrench device to be carried out as per the satisfcation of the EIC. Only Pipe bracings to be considered. Only Sag-angles to be considered. Standing Seam sheet thickness to be mentioned as 0.55mm Framed Openings for all cutouts for services, dec slabs, Windows, Doors and any other opening. PEB vendor needs to include details such as: 1) Primary Members: _____ Tons 2) Secondary Members: _________ Tons 3) PUF Panel: ____Sq.M 4) Wall Cladding Sheet: ___Sq.M 5) Roof: ____Sq.M Cherry Pickers, Boom Lifts, scissor lifts to be used by the Vendors for cladding wall sheet fixing both internal and external. ROOF EXTENSION & CANOPY – with Soffit Panel - Soffit panel to be provided in the entire canopy over the truck dock area and Garbage area/waste Holding area extended canopy. CAGE LADDER - 1 no. to access/egress Utility Block terrace & 1 no. for main roof access/egress from Ground floor. 1 No. of ladder from 1st floor terrace to top roof area to be provided. • Anchor bolts & templates to be supplied within 10 days of approval of GA drawings. • Supply & erection of supporting metal frames for insect killer, air curtains, FHC, fire exit doors& any other opening . • All foundation bolts to be painted with black Japan paint after building erection is completed/before pouring of concrete on it to avoid rusting of bolts.- All Bolts to be embedded in concrete and bolts not be visible over the Finished floor. • Purlins should be pre-holed, 12mm dia. At every 2m length to take the services hanger. Vendor to furnish the design calculations alongwith STAAD model etc. The quoted rate should be inclussive of all the items, No NT items/ additional claims.
SK-1 | Providing & fixing of 2mm Thk Polycarbonate Sky Lights with Mesh - 3.3 Mtr Length | Each | 1600 | 4720 | 7552000
SK-2 | Providing & fixing of 600mm Throat Turbo Ventilator PC Base with Mesh | Each | 2000 | 5310 | 10620000
| SUBHEAD: XI TOTAL : RS |  |  |  | 3218450080

## SD (hidden)
NAME OF WORK : PROPOSED E-BUS MANUFACTURING FACILITY AT SEETHARAMPURAM
SCHEDULE OF ITEMS
Item No. | DESCRIPTION | UNIT | RATE (Rs.) | AMOUNT | TOTAL QTY | AMOUNT
SUBHEAD-I :EARTH WORK & EXCAVATION :
E-1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means in foundation trenches or drains (not exceeding 1.5m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50M
a) | a) All kinds of soils | CUM | 100 | 3105000 | 85740 | 8574000
E-2 | Excavation work by mechanical means (Hydraulic excavator)/ manual means in foundation trenches or drains (not exceeding 1.5m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soils as directed, within a lead of 50 m.
a) | a) Ordinary Rock | CUM | 405 | 1257525 | 8574 | 3472470
b) | b) Hard Rock (Blasting Prohibited) | CUM | 540 | 1676700 | 8574 | 4629960
E-3 | Extra for every additional lift of 1.5 m or part thereof in excavation / banking excavated or stacked materials.
a) | a) All kinds of soils | CUM | 20 | 828000 | 44380.8 | 887616
E-6 | Filling with available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. | CUM | 50 | 0 | 36768 | 1838400
E-7 | Excavating, supplying and filling of local earth (including royalty) by mechanical transport upto a lead of 5km also including ramming and watering of the earth in layers not exceeding 20 cm in trenches, plinth, sides of foundation etc. complete. | CUM | 300 | 0 | 0 | 0
E-8 | Supplying and stacking at site
a | 90 mm to 45 mm size stone aggregate | CUM | 1743.84 | 0 | 0 | 0
b | 53 mm to 22.4 mm size stone aggregate | CUM | 1653.53 | 0 | 0 | 0
E-9 | Supplying and filling in plinth with sand under floors, including watering, ramming, consolidating and dressing complete. | CUM | 1350 | 0 | 0 | 0
| SUBHEAD: I TOTAL : RS |  |  | 6867225 |  | 19402446
SUBHEAD-II : PLAIN & REINFORCED CEMENT CONCRETE :
C-1 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :
a) | a) 1:4:8 (1 Cement : 4 coarse sand : 8 graded stone aggregate 40 mm nominal size) | CUM | 5694 | 432744 | 3406 | 19393764
C-2 | Providing and laying cement concrete in retaining walls, return walls, walls (any thickness) including attached pilasters, columns, piers, abutments, pillars, posts, struts, buttresses, string or lacing courses, parapets, coping, bed blocks, anchor blocks, plain window sills, fillets, sunken floor,etc., up to floor five level, excluding the cost of centering, shuttering and finishing:
a) | a) 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 40 mm nominal size) | CUM | 8438 | 0 | 84 | 708792
C-3 | Making plinth protection 50 mm thick of cement concrete 1:3:6 (1 cement: 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) over 75mm thick bed of dry brick ballast 40 mm nominal size, well rammed and consolidated and grouted with fine sand, including finishing the top smooth. | SQM | 614 | 0 | 0 | 0
C-4 | Providing and laying in position machine batched and machine mixed design mix M-30 grade cement concrete for reinforced cement concrete work, using cement content as per approved design mix, including pumping of concrete to site of laying but excluding the cost of centering, shuttering, finishing and reinforcement, including admixtures in recommended proportions as per IS: 9103 to accelerate, retard setting of concrete, improve workability without impairing strength and durability as per direction of Engineer-in-charge. (Note :- Cement content considered in this item is @ 330 kg/cum. Excess/ less cement used as per design mix is payable/recoverable separately).
| a) Foundations, rafts, footings, pedestal, Column, Walls below Finished Floor Level and like | CUM | 6500 | 2060500 | 8142 | 52923000
| b) Columns above Finished Floor Level and like | CUM | 7500 | 0 | 0 | 0
| c) Plinth Beams and like | CUM | 7500 | 0 | 0 | 0
| d) Lintels / Tie Beams, Sloped Beams and like | CUM | 7500 | 0 | 0 | 0
| e) Suspended floors / roofs, Sloped roofs, roof of cable /duct trenches and like. | CUM | 7500 | 0 | 2054 | 15405000
| f) Chajjas and like | CUM | 7500 | 0 | 0 | 0
| g) Staircase waist slabs, landings and steps and like | CUM | 7500 | 0 | 0 | 0
| h)Retaining wall | Cum | 7500 | 9105000 | 8254 | 61905000
C-6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete
a) | a) Thermo-Mechanically Treated bars (Fe 500 Grade) | MT | 80685 | 19679071.5 | 2294.16 | 185104299.6
C-7 | Centering and shuttering including strutting, propping etc. and removal of form for :
a) | Foundations, footings, bases of columns, etc. for mass concrete | SQM | 308 | 113960 | 5118 | 1576344
b) | Columns, Pillars, Piers, Abutments, Posts and Struts | SQM | 609 | 0 | 0 | 0
c) | Lintels, beams, plinth beams, girders, bressumers and cantilevers | SQM | 609 | 0 | 0 | 0
d) | Suspended floors, roofs, landings, balconies and access platform | SQM | 650 | 0 | 10800 | 7020000
e) | Weather shade, Chajjas, corbels etc., including edges | SQM | 700 | 0 | 0 | 0
f) | Stairs, (excluding landings) except spiral-staircases | SQM | 658 | 0 | 0 | 0
g) | Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc. | SQM | 670 | 3614650 | 35080 | 23503600
| SUBHEAD: II TOTAL : RS |  |  | 35005925.5 |  | 367539799.6
SUBHEAD-III : STONE & BRICK MASONRY :
M-1 | Random rubble masonry with hard stone in foundation and plinth including levelling up with cement concrete 1:6:12 (1 cement : 6 coarse sand : 12 graded stone aggregate 20 mm nominal size) upto plinth level with Cement mortar 1:6 (1 cement : 6 coarse sand) | CUM | 5989 | 0 | 11340 | 67915260
M-2 | Providing and laying autoclaved aerated cement blocks masonry with 150mm/230mm/300 mm thick AAC blocks in super structure above plinth level up to floor V level with RCC band at sill level and lintel level with approved block laying polymer modified adhesive mortar all complete as per direction of Engineerin- Charge. (The payment of RCC band and reinforcement shall be made for seperately). | CUM | 6296 | 0 | 1995 | 12560520
M-3 | Providing and laying autoclaved aerated cement blocks masonry with 100 mm thick AAC blocks in super structure above plinth level up to floor V level in cement mortar 1:4 (1 cement : 4 coarse sand ). The rate includes providing and placing in position 2 Nos 6 mm dia M.S. bars at every third course of masonry work. | CUM | 8002 | 0 | 0 | 0
| SUBHEAD: III TOTAL : RS |  |  | 0 |  | 80475780
SUBHEAD-IV : STEEL & WOOD WORKS :
W-1 | Fencing with angle iron post placed at required distance embedded in cement concrete blocks, every 15th post, last but one end post and corner post shall be strutted on both sides and end post on one side only and provided with horizontal lines and two diagonals interwoven with horizontal wires, of barbed wire weighing 9.38 kg per 100 m (minimum), between the two posts fitted and fixed with G.I. staples, turn buckles etc. complete. (Cost of posts, struts, earth work and concrete work to be paid for separately). Payment to be made per metre cost of total length of barbed wire used. | Kg | 90 | 0 | 12960 | 1166400
W-2 | Fencing with angle iron post placed at required distance embedded in cement concrete blocks, every 15th post, last but one end post and corner post shall be strutted on both sides and end post on one side only and provided with horizontal lines and two diagonals interwoven with horizontal wires, of barbed wire weighing 9.38 kg per 100 m (minimum), between the two posts fitted and fixed with G.I. staples, turn buckles etc. complete. (Cost of posts, struts, earth work and concrete work to be paid for separately). Payment to be made per metre cost of total length of barbed wire used. |  |  | 0 | 0 | 0
| With G.I. barbed wire | Rmt | 18 | 0 | 25196 | 453528
W-3 | Providing orange colour safety foot rest of minimum 6 mm thick plastic encapsulated as per IS : 10910, on 12 mm dia steel bar conforming to IS: 1786, having minimum cross section as 23 mmx25 mm and over all minimum length 263 mm and width as 165 mm withminimum 112 mm space between protruded legs having 2 mm tread on top surface by ribbing or chequering besides necessary and adequate anchoring projections on tail length on 138 mm as per standard drawing and suitable to with stand the bend test and chemical resistance test as per specifications and having manufacture's permanent identification mark to be visible even after fixing, including fixing in manholes with 30x20x15 cm cement concrete block 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) complete as per design. | Nos | 528 | 0 | 160 | 84480
| SUBHEAD: IV TOTAL : RS |  |  | 0 |  | 1704408
SUBHEAD-V : PLASTERING & SURFACE TREATMENT :
FN-1 | 6 mm thick plastering in cement mortar 1:3 (1 cement: 3 fine sand) at all levels and locations for all concrete surfaces of columns, beams and slabs finished smooth and even, etc., complete all as directed by Engineer - in - Charge. | SQM | 302 | 0 | 2100 | 634200
FN-2 | 15 mm thick plastering, in cement mortar 1:3 (1 cement :3 fine sand) finished neat with extra cement including benching etc. all as directed by Engineer - in - Charge. | SQM | 394 | 0 | 32460 | 12789240
FN-3 | 18 mm thick sand faced cement plastering on external surfaces of brick or concrete surfaces in two layers consisting of 6 mm thick cement mortar 1:3 (1 cement :3 fine sand) top coat mixed with integral water proofing compound over a base coat 12 mm thick cement mortar 1:5 (1 cement :5 coarse sand), finished sand face including providing and fixing 12mmx22mm gauge chicken mesh with all necessary hardware at the junction of RCC and brick work with overlapping of 100 mm on both sides, etc., complete at all levels and locations and as directed by Engineer - in - Charge. | SQM | 416 | 0 | 18070 | 7517120
FN-4 | White washing with lime on new walls and ceilings three coats to give an even shade including preparation of surfaces etc.,complete all as directed by Engineer - in - Charge. | SQM | 30 | 0 | 18012 | 540360
FN-5 | Providing and applying plaster of Paris putty of 2 mm thickness over plastered surface to prepare the surface even and smooth and applying 2 coats of oil bound distemper of approved brand and manufacture to give an even shade on new work of two or more coats over and including priming coat, etc., complete all as directed by Engineer - in - Charge. | SQM | 215 | 0 | 0 | 0
FN-6 | Providing and Finishing walls with textured exterior paint of required shade on new work (Two or more coats applied @ 3.28 ltr/10 sqm) over and including priming coat of exterior primer applied @ 2.20kg/ 10 sqm | SQM | 221 | 0 | 70 | 15470
FN-7 | Providing and applying two coats of synthetic enamel paint of approved brand and shade over a coat of primer including preparation of surface and applying approved brand putty on following surfaces at all levels and locations etc., complete all as directed by Engineer - in - Charge:
| a) Steel surfaces with zinc chromate primer | SQM | 169 | 0 | 576 | 97344
| b) Wooden surface with approved primer | SQM | 174 | 0 | 0 | 0
| SUBHEAD: V TOTAL : RS |  |  | 0 |  | 21593734
SUBHEAD- VI : FLOORING
F-1 | 52 mm thick cement concrete flooring with concrete hardener topping, under layer 40 mm thick cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) and top layer 12 mm thick cement hardener consisting of mix 1:2 (1 cement hardener mix : 2 graded stone aggregate 6 mm nominal size) by volume, hardening compound mixed @ 2 litre per 50 kg of cement or as per manufacturer’s specifications. This includes cost of cement slurry, but excluding the cost of nosing of steps etc., complete. | Sqm | 771 | 0 | 420 | 323820
F-2 | Cement skirting 150mm high in CM (1:3) 18mm thick finished with a floating coat of neat cement etc., complete. | Sqm | 514 | 0 | 2 | 1028
| SUBHEAD: VI TOTAL : RS |  |  | 0 |  | 324848
SUBHEAD- VII : Waterproofing
Terrace Waterproofing
WP-1 | Surface Preparation: RCC Surfaces must be clean, even and sound concrete. Remove all oil, dirt, laitance and other Contaminants by manually. Grout: Providing Chemical injection treatment in the form of pressure grouting to the cold joint by injecting cement slurry mixed with grout admixture ArmGrout Additive @ 250 gms per bag of cement, in the required consistency through the pre fixed PVC nozzles in the 10mm dia holes, fixing of PVC nozzles with quick setting compound ReArm Fix 10S and final cutting the projected nozzles and sealing off the PVC nozzles after the injection operation is over with quick setting compound ReArm Fix 10S, non-shrink rapid setting mortar compound, finishing, curing etc. as per manufacturers specification and as directed. (cement has to be supplied by the main contractor). Application of Primer: Apply FloArm primer 1260 over well prepared surface. Application of Hybrid Polyurea waterproof coating: Application of Polyurethane waterproof coating of two component, spray applied fast setting coating based out of modified polyurethane/ Hybrid Polyurea Hybrid to achieve an elastic, high crack bridging waterproofing coating with long life expectancy waterproofing system AquaArm Purtech H 1 manufactured and supplied by MYK Arment or equivalent. AquaArm Purtech H1 can be applied at 1Kg/Sqm/mm thickness. The membrane will have the following technical parameters: Elongation : >500 % Recovery from 100 % Elongation : >85% Tensile Strength : >12 N/mm2 | Sqm | 1650 | 0 | 0 | 0
Providing and laying 150 Gsm Geo fabric membrane as separation layer
Protection Screed for Horizontal Areas: Providing and Laying M20 grade screed concrete in 1:100 to a minimum thickness of 75 mm mixed with AquaArm Proof WP10 -Integral Waterproofing admixture at the dosage of 125 ml/bag of cement and virgin polypropylene fibrated fiber at 0.9kg/m3 ,over waterproofing layer to a minimum thickness of 75 mm as per site requirement (Civil Contractor Scope) including control joints of 4M X 4M size and filling the panels with polyurethane sealant ( SealArm PU).
Protective Plaster: Applying avg. 15 mm thick, CM 1:4 plaster admixed with AquaArm Proof WP-10, Integral Waterproofing Compound @ 150 ml / bag of cement. (Mode of measurement will be actual treated area). (cement and sand shall be supplied by the main contractor)
WP-2 | Waterproofing Treatment to Retaining Wall
a | Surface Preparation: (after de shuttering & curing) RCC Surfaces must be clean, even and sound concrete. Remove all oil, dirt, laitance and other Contaminants by manually. Construction joint treatment: Starter level lift joint, pour joints or critical joints in the wall make a “V” groove with 20mmx20mm width and depth. Fix the PVC Pipe of 10mm dia into the drilled hole and pack it tightly use quick setting cement - ReArmFix 10S. Packing the groove with non-shrink grout ArmGrout M65 Inject cementitious slurry by adding cement grout ArmGrout Additive maintaining W/P ratio of 0.45 with the dosage of 250gms/bag of cement under pressure through the nozzles. This should be applied before application of crystalline coating of AquaArm IC. Providing and applying crystlline waterproofing treatment to RCC retaining wall. The waterproofing to be carried out using AquaArm IC of MYK Arment make, by preparing AquaArm IC slurry, by adding 6.75 to 8 liter clean water per 25 kg of AquaArm IC. Both the components should be mixed with a mechanical stirrer (300 to 700 RPM) until a lump free, homogeneous slurry is obtained. The slurry should be applied with a brush @ 1.5 kg/Sqm in two coats on the concrete substrate. The second coat should be applied when the first coat is still tacky. | Sqm | 518 | 0 | 1204 | 623672
WP-3 | Toilets
| Surface Preparation: RCC Surfaces must be clean, even and sound concrete. Remove all oil, dirt, laitance and other Contaminants by manually. Grout: Providing Chemical injection treatment in the form of pressure grouting to the cold joint by injecting cement slurry mixed with grout admixture ArmGrout Additive @ 250 gms per bag of cement, in the required consistency through the pre fixed PVC nozzles in the 10mm dia holes, fixing of PVC nozzles with quick setting compound ReArm Fix 10S and final cutting the projected nozzles and sealing off the PVC nozzles after the injection operation is over with quick setting compound ReArm Fix 10S, non-shrink rapid setting mortar compound, finishing, curing etc. as per manufacturers specification and as directed. (cement has to be supplied by the main contractor) Waterproofing application: - Waterproofing application:- Providing and application of single component synthetic rubber based polymer dispersion which dries to form a seamless elastomeric waterproof membrane AquaArm Saniflex at a coverage of 1.2 kg /m2 over a primed surface with AquaArm UniPrimer-GE. The coating shall be carried out upto 300mm at wall areas. | Sqm | 782 | 0 | 0 | 0
Protective Plaster: Applying avg. 15 mm thick, CM 1:4 plaster admixed with AquaArm Proof WP-10, Integral Waterproofing Compound @ 150 ml / bag of cement. (Mode of measurement will be actual treated area). (cement and sand shall be supplied by the main contractor)
WP-4 | Bore Packing :- All the pipes to placed / inserted in the core cut areas, shall be rough with sand paper and apply a coat of bonding agent with ReArm SBR 45, around the cut bores. Grouting the gaps between the pipe and the core cutting by an expansive cementitious grout ArmGrout M-65 that shall be poured into the gaps after fixing in place an effective leak-free shuttering.
a | 75mm Dia | Nos | 352 | 0 | 0 | 0
b | 125mm Dia | Nos | 411 | 0 | 0 | 0
c | 160mm Dia | Nos | 470 | 0 | 0 | 0
| SUBHEAD: VII TOTAL : RS |  |  | 0 |  | 623672
SUBHEAD- VIII : Roads
RD-1 | Preparation and consolidation of sub grade with power road roller of 8 to 12 tonne capacity after excavating earth to an average of 22.5 cm depth, dressing to camber and consolidating with road roller including making good the undulations etc. and re-rolling the sub grade and disposal of surplus earthwith lead upto 50 metres. | Sqm | 162.9 | 0 | 115260 | 18775854
RD-2 | Banking excavated earth in layers not exceeding 20 cm in depth, breaking clods, watering, rolling each layer with ½ tonne roller, or wooden or steel rammers, and rolling every 3rd and top-most layer with power roller of minimum 8 tonnes and dressing up, in embankments for roads, flood banks, marginal banks, and guide banks etc., lead upto 50 m and lift upto 1.5 m in all kinds of soils. | Cum | 489.6 | 0 | 44240 | 21659904
RD-3 | Providing, laying, spreading and compacting graded stone aggregate (size range 53 mm to 0.075 mm ) to wet mix macadam (WMM) specification including premixing the material with water at OMC in for all leads & lifts, laying in uniform layers with mechanical paverfinisher in sub- base / base course on well prepared surface and compacting with vibratory roller of 8 to 10 tonne capacity to achievethe desired density, complete as per specifications and directions of Engineer-in-Charge. | Cum | 2523.29 | 0 | 24257 | 61207324
RD-4 | Cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 40 mm nominal size) in pavements, laid to required slope and camber in panels as required including consolidation finishing and tamping complete. | Sqm | 6660 | 0 | 15954 | 106253640
RD-5 | Providing and laying design mix cement concrete of M-30 grade, in roads/ taxi tracks/ runways, using cement content as per design mix, using coarse sand and graded stone aggregate of 40 mm nominal size in appropriate proportions as per approved & specified design criteria, providing dowel bars with sleeve/ tie bars wherever required, laying at site, spreading and compacting mechanically by using needle and surface vibrators, levelling to required slope/ camber, finishing with required texture, including steel form work with sturdy M.S. channel sections, curing, making provision for contraction/expansion, construction & longitudinal joints (10 mm wide x 50 mm deep) by groove cutting machine, providing and filling joints with approved joint filler and sealants, complete all as per direction of Engineer-in-charge (Item of joint fillers, sealants, dowel bars with sleeve/ tie bars to be paid separately).
| Cement concrete prepared with batch mixing machine | Cum | 8543.7 | 0 | 15954 | 136306190
| Cement concrete manufactured in automatic batching plant (RMC plant) i/c transportation to site in transit mixer | Cum | 9005.4 | 0 |  | 0
RD-6 | Providing and laying at or near ground level factory made kerb stone of M-25 grade cement concrete in position to the required line, level and curvature, jointed with cement mortar 1:3 (1 cement: 3 coarse sand), including making joints with or without grooves (thickness of joints except at sharp curve shall not to more than 5mm), including making drainage opening wherever required complete etc. as per direction of Engineer-in-charge (length of finished kerb edging shall be measured for payment). (Precast C.C. kerb stone shall be approved by Engineer-in-charge). | Cum | 7752.6 | 0 | 1434 | 11117229
RD-7 | Providing and laying 80mm thick faciory made cement concrete interlocking paver block of M -30 grade made by block makingmachine with strong vibratory compaction, of approved size, design & shape, laid in required colour and pattern over and including 50mm thick compacted bed of coarse sand, filling the joints with line sand etc. all complete as per the direction of Engineer-in-charge. | Sqm | 918 | 0 | 50081 | 45974358
RD-8 | Dry stone pitching 22.5 cm thick laid in courses and required profile with hammer dressed stones having no side less than 15 cm, with minimum depth of 20 cm including preparing the bedding surface etc. all complete. | Sqm | 488.7 | 0 | 3360 | 1642032
RD-9 | Providing and laying non-pressure NP2 class (light duty) R.C.C. pipes with collars jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 fine sand) including testing of joints etc., complete.
a | 150 mm dia. R.C.C. pipe | Rmt | 444.6 | 0 | 1330 | 591318
b | 300 mm dia. R.C.C. pipe | Rmt | 812.7 | 0 | 80 | 65016
c | 450 mm dia. R.C.C. pipe | Rmt | 1333.8 | 0 | 269 | 358793
d | 2000 mm dia. R.C.C. pipe | Rmt | 6300 | 0 | 320 | 2016000
RD-10 | Constructing brick masonry manhole in cement mortar 1:4 (1 cement : 4 coarse sand) with R.C.C. top slab with 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand : 8 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design : | Sqm | 6886.8 | 0 | 0 | 0
a | Inside size 90x80 cm and 45 cm deep including C.I. cover with frame (light duty) 455x610 mm internal dimensions, total weight of cover and frame to be not less than 38 kg (weight of cover 23 kg and weight of frame 15 kg), With Sewer bricks conforming to IS : 4885
RD-11 | Extra for depth for manholes :
| Size 90x80 cm, With Sewer bricks conforming to IS : 4885 | Rmt | 5344.2 | 0 | 0 | 0
RD-12 | Providing M.S. foot rests including fixing in manholes with 20x20x10 cm cement concrete blocks 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) as per standard design, With 20x20 mm square bar | Each | 276.3 | 0 | 0 | 0
RD-13 | Supply & Design of Tensile Membrane & Supporting Structure, Supply of Serge Ferrari Fabric, Fabrication of Membrane and connection systems, support MS structure, Installation of structural Membrane including fabric flashing and Connection system & tensioning and Painting the structure with One coat of Primer and Two coats of Enamel brush paint | Sqm | 4304 | 0 | 11429 | 49190416
| SUBHEAD: VIII TOTAL : RS |  |  | 0 |  | 455158074
SUBHEAD- I : Area Development
AD-1 | Excavating, supplying and filling of local earth (including royalty) by mechanical transport upto a lead of 2km also including ramming and watering of the earth in layers not exceeding 20 cm in trenches, plinth, sides of foundation etc. complete. | Cum | 100 | 0 | 450000 | 45000000
| SUBHEAD: I TOTAL : RS |  |  | 0 |  | 45000000
COST SUMMARY
I | EARTH WORK & EXCAVATION |  |  | 6867225 |  | 19402446
II | PLAIN & REINFORCED CEMENT CONCRETE |  |  | 35005925.5 |  | 367539799.6
III | STONE & BRICK MASONRY |  |  | 0 |  | 80475780
IV | STEEL & WOOD WORKS |  |  | 0 |  | 1704408
V | PLASTERING & SURFACE TREATMENT |  |  | 0 |  | 21593734
VI | FLOORING |  |  | 0 |  | 324848
VII | Waterproofing |  |  | 0 |  | 623672
VIII | Roads |  |  | 0 |  | 455158074
X | Area Development |  |  |  |  | 45000000
| TOTAL AMOUNT Rs. |  |  | 41873150.5 |  | 991822761.6
| Say Rs. |  |  | 41873151 |  | 991822762
|  |  |  | 41873151 |  | ###########
991822762
0

## Gardern
Landscaping works
Sl. No. | Description of work | Unit | Quantity | Rate (Rs) Incl.GST | Amount (in Rs.) Incl.GST
1 | Garden Soil: Supply, Stacking, Mixing in required proportions of 70:20:10 of red soil, manure, sand, up to 300 mm Lift and lead spreading and compacting as required maybe for all plantation works complete with gradient slopes and surface preparation | Sqm | 60000 | 225 | 13500000
2 | Supply & Lay the specified Mexican Lawn including cultivation, Dressing the surface to the desired shape, laying 6” layer of fine red soil, covered with a thin layer of sand, watering, rolling with hand roller (4” thickness after rolling), including the cost of for all plant cost, transport, soil preparation with Red Earth, Sand and Organic Fertilizers and pesticides are to be used as required/directed, labor charges, disposing the surplus earth and make good the area etc., complete | Sqm | 60000 | 322 | 19320000
3 | Trees: Excavating/constructing pits of size approximately 0.75m X 0.75m X 0.75m deep ; backfilling with Red Poyta soil and organic manure (@ 20 gms/pit/sqmt) (4:1) and providing mulch cover as per the instruction. Procuring and planting specified nursery Grown Trees of minimum 4mtr height , supporting it with sturdy stakes as per detail; put into the pit by the side of the saplings and tied to it. The spacing, location and other details as per the drawings and specifications. Rate to include for plant cost, transport, soil, preparation, installation, labor, disposing the surplus earth, , etc., all complete. Organic fertilizers and pesticides (@ 20 gms/pit/sqmt) are to be used as required/directed. | Each | 3000 | 2124 | 6372000
4 | Shrubs: Excavating/constructing pits approximately 450mm deep & planting of specified Shrubs including cultivation of land to a depth of 450mm, clearing of debris and unwanted materials and planting the same in a mixture of Red Poyta soil and organic manure (@ 20 gms/pit/sqmt) (4:1) and providing mulch cover as per the instruction. Procuring and planting nursery grown healthy and bushy ground cover plants, the spacing location and other details as per the drawings and specifications. Rate to include for all plant cost, transport, soil preparation, installation, labor, disposing the surplus earth, all complete. Organic fertilizers and pesticides are to be used as required/directed. | Each | 12000 | 229 | 2748000
5 | Ground Covers: Excavating/constructing pits approximately 450mm deep & planting of specified Ground Cover including cultivation of land to a depth of 450mm, clearing of debris and unwanted materials and planting the same in a mixture of Red Poyta soil and organic manure (@ 20 gms/pit/sqmt) (4:1) and providing mulch cover as per the instruction. Procuring and planting nursery grown healthy and bushy ground cover plants, the spacing location and other details as per the drawings and specifications. Rate to include for all plant cost, transport, soil preparation, installation, labor, disposing the surplus earth, all complete. Organic fertilizers and pesticides (@ 20 gms/pit/sqmt) are to be used as required/directed. | Each | 10000 | 66 | 660000
6 | Supply & Fix the ProGrass Grass pavers in 500mm*390mm*45mm size panels and honeycomb cell structure. Grass Pavers to be made of recyclable HDPE with approximate green area of about 90%. Make: Ritter Landscaping, Germany | Sqm | 5000 | 1770 | 8850000
7 | Manufacture, Supply, Delivery, of 110 mm dia Unplasticised PVCs Pipes including Lowering, laying, jointing and testing of pressure 6 kg/cm2 for potable water supplies conforming to IS : 4985/2000 (3rd revision) with bell ends (Socket) as per specification in light Grey/Natural Ivory Grey/ Any other Color (except White) inclusive of transportation to the sub-divisional stores anywhere in TS excluding taxes-PVC for main 6kg/cm2-110mm-WATERCARRIER SYSTEM | Rmt | 2000 | 226 | 452000
8 | Manufacture, Supply,Delivery, of 90mm dia Unplasticised PVCs Pipes including Lowering, laying, jointing and testing of pressure 6 kg/cm2 for potable water supplies conforming to IS : 4985/2000 (3rd revision) with bell ends (Socket) as per specification in light Grey/Natural Ivory Grey/ Any other Color (except White) inclusive of transportation to the sub-divisional stores anywhere in TS excluding taxes-PVC for main 6kg/cm2-90mm-WATERCARRIER SYSTEM | Rmt | 2000 | 156 | 312000
9 | Manufacture, Supply,Delivery, of 75mmdia Unplasticised PVCs Pipes including Lowering, laying, jointing and testing of pressure 6 kg/cm2 for potable water supplies conforming to IS : 4985/2000 (3rd revision) with bell ends (Socket) as per specification in light Grey/Natural Ivory Grey/ Any other Color (except White) inclusive of transportation to the sub-divisional stores anywhere in TS excluding taxes-PVC for main 6kg/cm2-75mm-WATERCARRIER SYSTEM | Rmt | 5000 | 109 | 545000
10 | Manufacture, Supply,Delivery, of 63mm dia Unplasticised PVCs Pipes including Lowering, laying, jointing and testing of pressure 6 kg/cm2 for potable water supplies conforming to IS : 4985/2000 (3rd revision) with bell ends (Socket) as per specification in light Grey/Natural Ivory Grey/ Any other Color (except White) inclusive of transportation to the sub-divisional stores anywhere in TS excluding taxes-PVC for main 6kg/cm2-63mm-WATERCARRIER SYSTEM | Rmt | 500 | 79 | 39500
11 | Manufacture, Supply,Delivery, of 50mm dia Unplasticised PVCs Pipes including Lowering, laying, jointing and testing of pressure 6 kg/cm2 for potable water supplies conforming to IS : 4985/2000 (3rd revision) with bell ends (Socket) as per specification in light Grey/Natural Ivory Grey/ Any other Color (except White) inclusive of transportation to the sub-divisional stores anywhere in TS excluding taxes-PVC for main 6kg/cm2-50mm-WATERCARRIER SYSTEM | Rmt | 500 | 49 | 24500
12 | Manufacture, Supply,Delivery, of 40mm dia Unplasticised PVCs Pipes including Lowering, laying, jointing and testing of pressure 6 kg/cm2 for potable water supplies conforming to IS : 4985/2000 (3rd revision) with bell ends (Socket) as per specification in light Grey/Natural Ivory Grey/ Any other Color (except White) inclusive of transportation to the sub-divisional stores anywhere in TS excluding taxes-PVC for main 6kg/cm2-40 mm-WATERCARRIER SYSTEM | Rmt | 2000 | 33 | 66000
II | Sprinkler and Acessories
13 | Supply,Fixing & commissioning of flexible online tubing, TUBE OD16MM CL2X400 MTR in Black colour pressure rating 1 bar including cost , conveyance of all materials and labour charges etc., complete as per SS-Sprinkler and Acessories | Rmt | 5000 | 11 | 55000
14 | Supply,Fixing & commissioning of emitter Non pressure compensating with self piercing barbs,flow rates 2LPH to 8LPH UV resistant colour coded with working pressure 1.0to 3.5bar XB including cost , conveyance of all materials and labour charges etc., complete as per SS DRIPPER 8 LPH-Sprinkler and Acessories | Rmt | 5000 | 2 | 10000
15 | Supply,Fixing & commissioning of flexible, inline tubing Drip Lateral with in built drippers of 4 lph @ 30cm spacing including cost , conveyance of all materials and labour charges etc., -Sprinkler and Acessories | Rmt | 5000 | 12 | 60000
16 | Supply,Fixing & commissioning of Stakes for fixing lateral on mound complete--Sprinkler and Acessories | No | 25000 | 2 | 50000
17 | Supply,Fixing & commissioning of End caps for closing the lateral lateral complete -Sprinkler and Acessories | No | 25000 | 2 | 50000
18 | Supply,Fixing & commissioning of take off Connects Drip Line and Blank Tubing to PVC Mainlines at Low Pressures including cost , conveyance of all materials and labour charges etc., complete-Take off -Sprinkler and Acessories | No | 25000 | 2 | 50000
19 | Supply,Fixing & commissioning of Gromate Connects Drip Line and Blank Tubing to PVC Mainlines at Low Pressures including cost , conveyance of all materials and labour charges etc., complete-Grommets-Sprinkler and Acessories | No | 25000 | 3 | 75000
20 | Supply,Fixing & commissioning of High Quality Barbs to Grab Tubing for a Secure Fit. Unique Barb Design to Reduce Insertion Force. Non - Obtrusive Black Colored Fittings of 16mm BARB X BARB JOINER including cost , conveyance of all materials and labour charges etc., complete-Joiners-Sprinkler and Acessories | No | 25000 | 3 | 75000
21 | Supply,Fixing & commissioning of High Quality Barbs Grab Tubing for a Secure Fit. Unique Barb Design to Reduce Insertion Force. Non - Obtrusive Black Colored Fittings of 16mm BARBX BARB ELBOW including cost , conveyance of all materials and labour charges etc., complete as per SSJ-TURBO AQUR/ LINE ELBOW 16 MM-Sprinkler and Acessories | No | 25000 | 3 | 75000
22 | Supply,Fixing & commissioning of High Quality Barbs Grab Tubing for a Secure Fit. Unique Barb Design to Reduce Insertion Force. Non - Obtrusive Black Colored Fittings of 16mm BARBX BARB TEE including cost , conveyance of all materials and labour charges etc., complete as per SSJ-TURBO AQUR/ LINE TEE 16 MM-Sprinkler and Acessories | No | 25000 | 4 | 100000
23 | Supply,Fixing & commissioning of Pop up sprinkler full/part circle SPR. 565 POP STAR PLUS 3/4" having radius of throw 6.7m - 12m & flow of 0.09 - 0.61 ltr./sec.at an operative pressure of 2.5 - 4.5 kg/cm.sq. , The sprinkler is gear driven rotary type with RC technology having 3/4" bottom inlet, with slip clutch mechanism and heavy duty retract spring. memory arc .The sprinkler shall have multi-function, pressure-activated wiper seal for low pressure opreation a The sprinkler shall have internal Seal - A - Matic device which prevents low head drainage (upto 3.1m) & hence puddling & erosion. The body of sprinkler is of non - corrodible, heavy duty, ABS plastic.5004 including cost , conveyance of all materials and labour charges etc., complete-SPR. 565 POP STAR PLUS 3/4"-Sprinkler and Acessories | No | 500 | 773 | 386500
24 | Supply,Fixing & commissioning of 3/4" Pop up Connecting Swing joint Assembly 3/4"X30 CM STND.SWING JOINT,4S.E. The tubing shall be made of polyetylene having wall thickness of 2.3mm ,a working pressure of 5.5 kg/cm2 at 43oC and a surge pressure of 16.6 kg/cm2. The fittings shall be made of UV resistant thermo plastic.SA Series i including cost , conveyance of all materials and labour charges etc., complete-Sprinkler and Acessories | NO | 500 | 157 | 78500
25 | Supply,Fixing & commissioning of PVC SERVICE SADDLE 50 MM X3/4"- HD of varying size with pressure rating of PN 10 including cost , conveyance of all materials and labour charges etc., complete-Sprinkler and Acessories | No | 500 | 54 | 27000
26 | Supply,Fixing & commissioning of PVC SERVICE SADDLE 63 MM X 25MM(3/4)- HD of varying size with pressure rating of PN 10 including cost , conveyance of all materials and labour charges etc., complete-Sprinkler and Acessories | No | 500 | 70 | 35000
27 | Supply,Fixing & commissioning of Imported PVC SERVICE SADDLE40 MM X 25MM(3/4)- HD of varying size with pressure rating of PN 10 including cost , conveyance of all materials and labour charges etc., complete-Sprinkler and Acessories | No | 500 | 50 | 25000
28 | Providing of Pop-up Rotor Sprinkler of throw radius varying form 18-19 mts with key features like Plastic riser. Automatic Arc Return, Non trippable Drive Mechanism, Quick Check Arc Mechanism, Drain Check Valve, part & Full Circle in one nodel Model: I-25-04-B Pop-up Sprinkler Nozzle No 25, Pressure-4.5 kg/cm2, Radius-20.1m, Discharge-1.55 LPS -Sprinkler and Acessories | No | 100 | 1738 | 173800
29 | Providng 1” Pop up connecting Swingjoint Assemble. The tubing shall bemade of polyetylene having wallthickness of 2.3mm. a working pressureof 5.5 kg/ cm2 at 430C and a surge pressure of 16.6 Kg/ cm2. The fittingssahll be made of UV resistant thermopalstic. Swing Joint - 1" x 30 cm-Swing Joint - 1" x 30 cm-Sprinkler and Acessories | No | 500 | 389 | 194500
30 | Supply,Fixing & commissioning of control Valve, 3"Butterfly Valve in mainline for bypass and flow diversion of approved quality with pressure rating of PN 10 including cost , conveyance of all materials and labour charges etc., complete as per SSBUTTERFLY VALVE C.I. 80 MM -3”-Sprinkler and Acessories | No | 200 | 2368 | 473600
31 | Supply,Fixing & commissioning of PVC Service Saddle - 75 mm x 1” (Heavy Duty) of varying size with pressure rating of PN 10 including cost , conveyance of all materials and labour charges etc., complete -Sprinkler and Acessories | No | 500 | 87 | 43500
32 | Supply,Fixing & commissioning of PVC Service Saddle - 90 mm X 1" (Heavy Duty) of varying size with pressure rating of PN 10 including cost , conveyance of all materials and labour charges etc., complete-Sprinkler and Acessories | No | 500 | 110 | 55000
33 | Supply,Fixing & commissioning of PVC PVC Service Saddle - 110 mm X 1" (Heavy Duty) of varying size with pressure rating of PN 10 including cost , conveyance of all materials and labour charges etc., complete-Sprinkler and Acessories | No | 500 | 102 | 51000
34 | Providing & fixing of PS Utra Pop up POP UP MINISTER 4"WITH VAN 17A 1/2" having colour coded Spray nozzle of covering 1.5-5m. The Spray Head body shall be constructed of heavy-duty, ultraviolet resistant plastic and stainless steel spring with mutifunctional wiper seal with small exposed cover. etc. item complete-Sprinkler and Acessories | No | 500 | 274 | 137000
35 | Supply,Fixing & commissioning of PVC SERVICE SADDLE 63MM X 1/2"- HD of varying size with pressure rating of PN 10 including cost , conveyance of all materials and labour charges etc., complete-Sprinkler and Acessories | No | 500 | 54 | 27000
36 | Providing & Fixing of , 1/2" Pop up Connecting Four Elbow Swing joint Assembly. The fittings shall be made of UV resistant thermo plastic.etc. item complete.1/2"X30 CM STND.SWING JOINT,4S.E-Sprinkler and Acessories | No | 500 | 119 | 59500
37 | Providing and fixing of PVC SERVICE SADDLE 50 MM X1/2"- HD of varying size- HD-Sprinkler and Acessories | No | 5000 | 54 | 270000
38 | Providing and fixing of PVC SERVICE SADDLE 40 MM X1/2"- HD of varying size- HD-Sprinkler and Acessories | No | 5000 | 54 | 270000
39 | Supply,Fixing & commissioning of PVC CTRL VALV 90MM TEFLON SEAL PLAIN,security pivot to maintain lever in space,double water tight joint,direct injection stem non mechanical ,with a base which permits maximum penetration into the valve of size 63mm with pressure rating PN 10 including cost , conveyance of all materials and labour charges etc., complete -Sprinkler and Acessories | No | 600 | 2000 | 1200000
40 | Supply,Fixing & commissioning of PVC CTRL VALV75MM TEFLON SEAL PLAIN,security pivot to maintain lever in space,double water tight joint,direct injection stem non mechanical ,with a base which permits maximum penetration into the valve of size 63mm with pressure rating PN 10 including cost , conveyance of all materials and labour charges etc., complete-Sprinkler and Acessories | NO | 500 | 939 | 469500
41 | Supply,Fixing & commissioning of PVC CTRL VALV 63MM TEFLON SEAL PLAIN,security pivot to maintain lever in space,double water tight joint,direct injection stem non mechanical ,with a base which permits maximum penetration into the valve of size 63mm with pressure rating PN 10 including cost , conveyance of all materials and labour charges etc., complete-Sprinkler and Acessories | No | 500 | 696 | 348000
42 | Supply,Fixing & commissioning of self-closing flushing valves that are installed at the end of the irrigation line for effecting flushing of the line at the beginning of every irrigation cycle, thus avoiding the clogging of the emitters /sprinklers through removal of particles, sediments and other impurities from the water including cost , conveyance of all materials and labour charges etc., complete FLUSH VALVE 50 MM-Sprinkler and Acessories | No | 500 | 71 | 35500
43 | Supply,Fixing & commissioning of 12" IRRIGATION VALVE BOX 12" with greenlid and corrugated structure with unique shovel access slot and bolt hole knockout & having Dimensions @ Top Opening:18 1/4" L X 13" W & bottom opening :21 1/4" L X 15 15/16"W X 12" H PVB/VB including cost , conveyance of all materials and labour charges etc., complete -Valve and Filters Accessories | NO | 100 | 1779 | 177900
III | Valve and Filters Accessories
44 | Supply of Fixing & commissioning of 3"-80MM(3) SIN WITH M.MF. sandfilter with capacity 50 m3 / Hr matching pump design flow having an suitable inlet connections and backwash assembly for removal of algae, trash, silt at regular interval in the incoming water, with fine sand media bottom of filter & maximum working pressure of 7 Bars-Valve and Filters Accessories | No | 100 | 42256 | 4225600
45 | Supply,Fixing & commissioning of 3" DIS/SIS J-SUP-FLOW FIL FLAN 50M3 90MM G with capacity 50m3/Hr having an suitable inlet connections , to create a helical effect in the incoming water ,spinning particulate in suspension away from the filtering element and so minimizing cleanings frequency ,3/4" outlet for flushing at bottom of filter & maximum working presure of 12 Bars.STF including cost , conveyance of all materials and labour charges etc., complete-Valve and Filters Accessories | No | 50 | 6407 | 320350
46 | Supply of 2"PRESSURE GUAGE GLYCERINE FILLED &CORK 1/4"pressure guage glycrine filled & cork 1/4"-Valve and Filters Accessories | No | 200 | 414 | 82800
47 | Supply,Fixing & commissioning of 3"GM. NON RETURN VALVE 3." AP to prevent back flow have flap type or spring type with pressure rating of PN 10 including cost , conveyance of all materials and labour charges etc., complete-Valve and Filters Accessories | No | 100 | 4679 | 467900
48 | Supply,Fixing & commissioning of a DBL ACT AIR/VAC RELE VLV32MM(1)+D3750 " Air release valve The Air release valve shall be capable of both releasing and admitting air from and into the line. The working pressure shall be 5 bar including cost , conveyance of all materials and labour charges etc., complete-Valve and Filters Accessories | No | 100 | 529 | 52900
49 | Supply,Fixing & commissioning of QUICK COUPLING VL. 3/4"FEMALE made up of solid brass with locking cover corrosion resistant and stainless steel spring 3RC including cost , conveyance of all materials and labour charges etc., complete-Valve and Filters Accessories | No | 100 | 726 | 72600
50 | Supply,Fixing & commissioning of QUICK COUPLING KEY 3/4" Mthreads into top of QCV to provide water access 33DK including cost , conveyance of all materials and labour charges etc., complete-Valve and Filters Accessories | No | 100 | 302 | 30200
|  |  | Total |  | 63279150

## Sheet1 (hidden)
Civil | 3218450080
Garden | 63279150
Furniture | 19065000
kitchen | 3907050
Electrical | 558811860
plumbing | 25304340
fire | 127951770
hvac | 13321995
4030091245

## furniture
FURNITURE
S No | Item & Description | Unit | Qty | Rate (Rs) Incl.GST | Amount (in Rs.) Incl.GST
1 | Cabin Table CBT1 Material: Legs::25mm E1 grade PLPB Top:25mm E1 grade PLPB Modesty:18mm E1 grade PLPB Side Unit:18/9MM E1 grade PLPB with 3 drawers and 1 door Edgebanding: PVC Cable Manager:60MM PVC gourmet Table Size 1800 x 900 x 750 H Side Unit:900x450 x 650H Color: HSN: 940306 | Nos | 20 | 45000 | 900000
2 | Cabin Table-CBT5 Table Size:1800*900*750H Side Unit:1800*450*650H Material: MS Leg as per Design-Powder coated Top:25mm E1 grade PLPB with PVC Edgebanding Side Unit:18/9mm E1 grade PLPB with PVC Edgebanding 2 drawers,2doors ,1 Dummy Modesty: PLPB/MS Powder coated as per design HSN: 9403 | Nos | 5 | 35000 | 175000
3 | Cabin Table-CBT6 MS legs with powder coating 25mm PLPB top 18mm PLPB modesty 18/9MM PLPB Storage with 3 drawers and 1 door Table Size 1500 x 750 x 750 H Side Unit:900x450 x 750H HSN: 940306 | Nos | 20 | 32000 | 640000
4 | Conference Table MS Legs as per design-CT3 25MM PLPB Top as per design Size 3000*1200*750H Price excluding POP Up boxes Seating Capacity-4+4+1+1 HSN: 9403 | Nos | 10 | 35000 | 350000
5 | Conference Table-CFT-V HSN: 9403 | Nos | 2 | 100000 | 200000
6 | Conference Table-CFTR Table Top Size 3000 x1200x750H Seating capacity-4+4+1+1 Material: PLPB Top shape: Rectangle Top Colors: Single Color as per selection-Vertical grains HSN: 9403 | Nos | 2 | 55000 | 110000
7 | Hexagonal Workstations-Opendesk Made with 50X25MS Legs and Beams with powder coating finish MS sheet Molded raceway with switchboard cutouts 60mm PVC Gourmet for each seat for cable manager 25mm PLPB Top with PVC edge banding 8mm thick 300mm height glass dividers with Brackets Price Excluding CPU trolley, Keyboard tray, Pedestal Unit, electrical and networking works Size: As per the drawing HSN: 9403 | Nos | 300 | 22000 | 6600000
8 | Reception Table-RT2- Size:L2400 x D675 x 750+300H 3drawer Pedestal-1no Material: PLPB Color Combination: As per Selection HSN: 940306 | Nos | 1 | 45000 | 45000
9 | Reception table-RT3, Material:E1 Grade PLPB Edge lipping: PVC Gourmet:60mm PVC Pedestal unit-3 drawers-E1 grade PLPB Color combination: as per selelct ion Size:1500 L x+600+750+300H HSN: 9403 | Nos | 1 | 45000 | 45000
10 | Chair-Dynamic-MB MESH BACK ADJUSTABLE ARMREST WITH PU PAD SYNCHRO TILT MECHANISM GASLIFT 100MM (BIFMA CERTIFIED) NYLON BASE NYLON CASTER (BIFMA CERTIFIED) 1year Warranty HSN: 940306 | Nos | 500 | 5000 | 2500000
11 | Chair-Mystic-HB "BUTTERFLY MESH BACK ADJUSTABLE HEADREST ADJUSTABLE LUMBAR SUPPORT ADJUSTABLE ARMREST WITH PU PAD, PU MOULDED CUSHION SEAT SYNCHRO TILT MECHANISM Class 4 gas lift 100MM ( BIFMA CERTIFIED) | Nos | 50 | 6500 | 325000
12 | Chair-HYBA-Highback-F1 PU-Imported Premium and Comfortable Executive Chair with Ergonomic Lumbar Support Internal Frame Material: Glass Filled Nylon Structure, Upholstery cover: PU Leatherette ¦ Color: Black ¦ Seat: Moulded with 45 density ¦ Size: High Back Armrest: Premium Aluminium Arms with Soft PU padding on the top ¦ Mechanism: Heavy Duty Any Position Lock Mechanism ¦ Gaslift: Class 3 (Pneumatic seat height adjustment) ¦ Base: Aluminium Base ¦ Castors: 60 mm Nylon wheels Maximum Weight Load: 120 kgs. Assembly: The product needs Complete Assembly. No machine required to assemble. Color: Black/Grey/Red/Navy blue HSN: 940306 | Nos | 30 | 25000 | 750000
Cafetaria
13 | Pantry Table-1 Size 1200*750*750H MS legs with powder coating 25mm PLPB top with PVC edge banding. Seating capacity -4nos HSN: 9403 | Nos | 250 | 6500 | 1625000
14 | Marvel Shell HSN: 9403 | Nos | 1000 | 1600 | 1600000
15 | Auditorium Chairs SAC: | Nos | 200 | 16000 | 3200000
|  |  |  | Tota | 19065000

## Kitchen eqp
KITCHEN EQUIPMENT
Sl.No | Description | Over all size | Qty | Rate (Rs) Incl.GST | Amount (in Rs.) Incl.GST
BULK COOKING AREA
1 | Steam boiler Tube design |  | 2 | 82500 | 165000
2 | Steam vessel (Rice) | Cap 50 litres | 2 | 24200 | 48400
3 | Steam vessel (Sambar) | Cap 50 litres | 2 | 24200 | 48400
4 | Steam vessel (Rasam) | Cap 50 litres | 2 | 24200 | 48400
5 | Steam vessel (Milk) | Cap 50 litres | 2 | 41800 | 83600
6 | Idly boiler | Cap. 180 idlys | 2 | 52800 | 105600
7 | Work table with sink | 48”x24”x34”+6” | 1 | 24200 | 24200
8 | 3 burner cooking range | 72”x24”x18” | 2 | 39600 | 79200
9 | Single sink unit | 24”x24”x34”+6” | 1 | 13200 | 13200
10 | 2 burner cooking range | 48”x24”x34” | 1 | 26400 | 26400
11 | 2 burner Chinese cooking range | 48”x30”x34” | 1 | 33000 | 33000
12 | Ms Dosa plate with SS body | 48”x24”x34” | 1 | 24200 | 24200
13 | Batter table | 24”x24”x34” | 1 | 9900 | 9900
14 | Bulk cooking range | 30”x30”x28” | 1 | 16500 | 16500
15 | Work table with sink | 48”x24”x34”+6” | 2 | 24200 | 48400
16 | Work table with Overhead shelve and under shelve | 60”x24”x34”+18” | 6 | 28600 | 171600
17 | Work table with one bottom shelve | 48”x24”x34” | 2 | 24200 | 48400
18 | Civil tandoor | 36”x36”x34” | 1 | 16500 | 16500
19 | Mable top table for tandoor | 36”x24”x34” | 1 | 13200 | 13200
20 | Chapati plate with puffer | 48”x30”x34” | 1 | 27500 | 27500
21 | Bain Marie counter 6 GN Pan container of 10 litres capacity | 48”x24”x34” | 2 | 49500 | 99000
22 | Room service trolley | 36”x24”x40” | 6 | 24200 | 145200
VEG PREPRATION AREA
23 | 2 sink unit | 48”x24”x34” | 1 | 26400 | 26400
24 | Cutting table | 48”x24”x34” | 1 | 24200 | 24200
25 | Veg cutting machine | Cap 100kg/hr | 1 | 41800 | 41800
26 | Work table | 48”x24”x34” | 3 | 26400 | 79200
27 | Storage rack | 44”x18”x72” | 2 | 30800 | 61600
NON VEG PREPRATION AREA
28 | Work table with sink | 48”x24”x34” | 1 | 24200 | 24200
29 | Work table | 36”x24”x34” | 1 | 19800 | 19800
30 | Meat mincer | Cap 50kgs/Hr | 1 | 26400 | 26400
31 | 2 Door under counter freezer | 60”x24”x34” | 1 | 49500 | 49500
32 | Cutting table | 48”x24”x34” | 1 | 24200 | 24200
33 | Cutting table | 36”x24”x34” | 1 | 19800 | 19800
ROOM SERVICE MATERIAL DEPOSIT AREA
34 | Storage rack | 44”x18”x72” | 3 | 30800 | 92400
35 | Water cooler | Cap 80 litres | 4 | 30800 | 123200
36 | Glass & jug holding rack | 36”x24”x72” | 4 | 26400 | 105600
37 | Sterilizing compartment | 48”x24”x34” | 3 | 41800 | 125400
38 | SS Banquet folding table | 48”x30”x30” | 10 | 5445 | 54450
GRINDING AREA
39 | Wet grinder | Cap 15 lit | 2 | 30800 | 61600
40 | Wet grinder | Cap 10 Lit | 1 | 26400 | 26400
41 | Potato peeler | Cap 20 Kgs | 1 | 38500 | 38500
42 | Single sink unit | 24”x24”x34”+6” | 1 | 13200 | 13200
43 | Dough kneader | Cap 40 lit | 1 | 38500 | 38500
DISH WASH AREA
44 | Soiled dish landing table with chute | 48”x24”x34” | 1 | 19800 | 19800
45 | Loading table with middle and bottom shelve | 48”x24”x34” | 1 | 24200 | 24200
46 | 3 sink unit | 72”x24”x34” | 1 | 39600 | 39600
47 | Supporting table for sink | 48”x12’x34” | 1 | 15400 | 15400
48 | Unloading table with middle and bottom shelve | 48”x24”x34” | 1 | 24200 | 24200
49 | Plate rack | 30”x24”x72” | 2 | 26400 | 52800
50 | Pot rack | 48”x24”x60” | 2 | 28600 | 57200
PANTRY AREA
51 | Tea burner | 36”x18”x14” | 1 | 13200 | 13200
52 | Work table with sink | 48”x24”x34” | 1 | 24200 | 24200
53 | 2 door under counter freezer | 60”x24”x34” | 1 | 49500 | 49500
54 | Work table with one bottom shelve | 48”x24”x34” | 1 | 24200 | 24200
CONTINENTAL COOKING AREA
55 | Civil tandoor | 36”x36”x34” | 1 | 16500 | 16500
56 | Mable top table for tandoor | 36”x24”x34” | 1 | 13200 | 13200
57 | 4 burner continental cooking range with oven below | 36”x36”x34” | 1 | 35200 | 35200
58 | Deep far fryer | 24”x24x34” | 1 | 19800 | 19800
59 | Work table with sink | 48”x24”x34” | 1 | 24200 | 24200
60 | Work table with sink | 60”x24”x34” | 1 | 26400 | 26400
61 | 2 door under counter freezer | 60”x24”x34” | 1 | 49500 | 49500
62 | 2 Burner Chinese cooking range | 90”x30”x34” | 1 | 49500 | 49500
63 | Bar BQ Grill | 3”x18”x34” | 1 | 19800 | 19800
64 | Chicken Griller | Std | 1 | 49500 | 49500
65 | Salamander | 30”x14”x14” | 1 | 26400 | 26400
66 | Work table with under shelve | 60”x24”x34” | 1 | 30800 | 30800
67 | Work table with under shelve | 48”x24”x34” | 1 | 24200 | 24200
68 | Work table with sink | 48”x24”x34” | 1 | 24200 | 24200
69 | Work table | 48”x24”x34” | 1 | 22000 | 22000
70 | Storage rack | 36”x24”x72” | 1 | 26400 | 26400
EXHAUST DUCTING SECTION
71 | SS HOODS PER RFT fabrication in 22 SWG SS 202 GRADE Sheet Per Rft | 70 rft | 70 | 6000 | 420000
72 | EXHAUST DUCTING IN GI PER SFT fabrication in 24 SWG Gi Sheet Per Sft | 1000 sft | 1000 | 120 | 120000
73 | BLOWER WITH 3HP CAPACITY |  | 2 | 54000 | 108000
GAS PIPE LINE SECTION
74 | LPG pipe line including 10X10 cylinder manifold set consisting of manifold pipes, manifold valves, flexible cylinder pigtails high pressure regulator main isolation valves etc, including MS ERW Class C pipe line of ½” size approximate 100 rft | 100 rft | 1 | 45000 | 45000
STEAM PIPE LINE SECTION
75 | Steam pipe line connecting rice cooker and idly box,steam generator with necessary fittings like valves, coupling, unions, tees, elbows, thread nipples, GI Pipe line of ¾” size TATA B class and pipe outer insulated with asbestos rope size approximate 100 rft | 100 RFT | 1 | 40000 | 40000
|  |  |  | Total | 3907050

## HVAC
HVAC WORKS
S.No | Description of work | Unit | Qty | Rate (Rs) Incl.GST |  | Amount (in Rs.) Incl.GST
| HVAC SYSTEM |  |  | Supply Rate (Rs) | Installation Rate (Rs) | Supply Amount (Rs) | Installation Amount (Rs) | Total Amount (Rs)
A | VARIABLE REFRIGERANT FLOW SYSTEM
1 | Supply & Installation, testing and commissioning of Outdoor units consists of 100% inverter compressors, inverter fan motor with aero-spiral fan blade and, e-pass heat exchanger, safety valves, solenoid valves, receiver, capillary tube, check valve, electronic expansion valve, high pressure switch, low pressure sensor, pressure regulating valve, refrigerant filter, stop valve, accumulator and refnet kits. The EER of VRF system shall be minimum 14.5 at AHRI condition. Rate shall be inclusive of R-410A refrigerant & oil pre charging, vibration isolators, supports, necessary foundation / pedestal works etc.The unit shall be sized to deliver followinr rated capacities minimum which excludes de-rated capacity due to excess length of refrigeration pipes, different elevation and the ambient temperature of 45 deg C & indoor 23 deg C. All Outdoor units shall be supplied along with Anti corrosive protection coating to prevent from chemicals/sea air/effluent water etc..
a | 66HP (14HP+22HP+30HP) | Nos | 1 | 1183840 | 79500 | 1183840 | 79500 | 1263340
b | 72HP (20HP+22HP+30HP) | Nos | 2 | 1341000 | 79500 | 2682000 | 159000 | 2841000
2 | Supply Installation Testing & commissioning of VRF indoor type units of the following capacities including shifting, drain pump, supports, etc. The following capacities shall be actual delivered capacity considering the actual operating conditions. Indoor unit shall be switched off on receipt of fire signal from fire alarm control module. Wiring from control module shall be considered.
i | 4-WAY CASSETTE UNIT
a | 3.5 TR | Nos | 6 | 44800 | 4200 | 268800 | 25200 | 294000
b | 3.0 TR | Nos | 4 | 43400 | 4200 | 173600 | 16800 | 190400
d | 1.6 TR | Nos | 5 | 38870 | 4200 | 194350 | 21000 | 215350
ii | 1-WAY CASSETTE UNIT | [5 empty] | - | -
b | 1.6 TR | Nos | 3 | 45300 | 4200 | 135900 | 12600 | 148500
c | 1.0 TR | Nos | 26 | 29666 | 4200 | 771316 | 109200 | 880516
e | 0.6 TR | Nos | 14 | 29666 | 4200 | 415324 | 58800 | 474124
iii | ROUND CASSETTE UNIT | [5 empty] | - | -
a | 4.0 TR | Nos | 20 | 53200 | 4200 | 1064000 | 84000 | 1148000
b | 3.0 TR | Nos | 11 | 50400 | 4200 | 554400 | 46200 | 600600
c | 2.5 TR | Nos | 7 | 48450 | 4200 | 339150 | 29400 | 368550
3 | Supply, installation, testing and commissioning of following refnet Y-Joints | [5 empty] | - | -
i | Indoor Refnet joints | Nos | 108 | 5200 | 600 | 561600 | 64800 | 626400
ii | Out door refnet joints | Nos | 4 | 8500 | 900 | 34000 | 3600 | 37600
4 | Supply of BACnet to compatible Network Interface and Central Remote Controller for monitoring and Controlling the VRF equipments by third party BMS. Rate shall inclusive of required hardware, software, Auto ON provision for critical areas based on temperature rise, sensors, etc. | Lot | 1 | 98500 | 6500 | 98500 | 6500 | 105000
5 | Supply and laying of 2C x 1.0 Sqmm multi standard screened cable with required size of GI conduit & accessories for VRV communications. | Rmt. | 700 | 215 | 35 | 150500 | 24500 | 175000
6 | SITC of copper refrigerant piping of various sizes with VRF Grad hard drawn/Soft copper piping necessary supports, fittings and clamps, insulation with 19 mm thk class 'O' nitrile rubber insulation with FM approval. Copper piping shall be of VRF grade with 100% eddy current testing. All wall crossings with proper PVC sleeve. all copper pipe run in a cable tray. |  |  |  |  | - | - | -
a | 6.4mm Dia with 19mm thick insulation | Rmt. | 250 | 404 | 160 | 101000 | 40000 | 141000
b | 9.5mm Dia with 19mm thick insulation | Rmt. | 390 | 495 | 160 | 193050 | 62400 | 255450
c | 12.7mm Dia with 19mm thick insulation | Rmt. | 285 | 345 | 160 | 98325 | 45600 | 143925
d | 15.9mm Dia with 19mm thick insulation | Rmt. | 415 | 690 | 160 | 286350 | 66400 | 352750
e | 19.1mm Dia with 19mm thick insulation | Rmt. | 90 | 890 | 180 | 80100 | 16200 | 96300
f | 22.2mm Dia with 19mm thick insulation | Rmt. | 80 | 960 | 180 | 76800 | 14400 | 91200
g | 25.4mm Dia with 19mm thick insulation | Rmt. | 30 | 1240 | 180 | 37200 | 5400 | 42600
h | 28.6mm Dia with 19mm thick insulation | Rmt. | 80 | 1397 | 200 | 111760 | 16000 | 127760
i | 31.8mm Dia with 19mm thick insulation | Rmt. | 60 | 1545 | 200 | 92700 | 12000 | 104700
j | 34.9mm Dia with 19mm thick insulation | Rmt. | 40 | 1949 | 200 | 77960 | 8000 | 85960
k | 38.1mm Dia with 19mm thick insulation | Rmt. | 20 | 2136 | 220 | 42720 | 4400 | 47120
l | 41.3mm Dia with 19mm thick insulation | Rmt. | 80 | 2317 | 220 | 185360 | 17600 | 202960
m | 44.5mm Dia with 19mm thick insulation | Rmt. | 60 | 2465 | 220 | 147900 | 13200 | 161100
n | 54.0mm Dia with 19mm thick insulation | Rmt. | 80 | 2950 | 240 | 236000 | 19200 | 255200
7 | Supply and erection of following sizes powder coated perforated cable tray made out of 18G thick GI sheet secured with GI clamps and brackets with adequate number of supports for pipes every 2.5 mts interval and at bends for Insulated refrigerant pipe for exposed areas |  |  |  |  | - | - | -
a | 300mm wide | Rmt. | 80 | 890 | 250 | 71200 | 20000 | 91200
8 | Providing and fixing in position the following Heavy Duty PVC pipe for drain with all joints, reducer, necessary elbows and tees, supporting arrangements, etc. Rate shall inclusive of thermal insulation with 9mm thickness Aluminium foil faced closed cell nitrile rubber tubular insulation |  |  |  |  | - | - | -
c | 32 NB | Mtrs | 220 | 265 | 90 | 58300 | 19800 | 78100
d | 25 NB | Mtrs | 345 | 195 | 90 | 67275 | 31050 | 98325
9 | Pressure testing, vacuumising of total VRF System piping etc. | Ckt | 4 |  | 35000 | - | 140000 | 140000
10 | Supply, installation, testing and commissioning of initial Charge of refrigerant gas - R 410 A . | Kgs | 320 | 890 | 150 | 284800 | 48000 | 332800
11 | Supply installation & testing commissioning of OUT DOOR Stand | No's | 9 | 8500 | 1500 | 76500 | 13500 | 90000
B | AIR DISTRIBUTION SYSTEM |  |  |  |  | - | - | -
12 | SITC of factory fabricated GSS Ducting with GI bolt & nuts, necessary supporting arrangement using GI full threaded rods and slotted rail. Ducting shall include guide vanes, etc., Ducting shall be designed for 500pa ESP as per the SMACNA-2005 & specifications of the following gauges. |  |  |  |  | - | - | -
a | 0.80 mm thick (22 Gauge) – Galvanized Sheet metal | Sqm. | 150 | 1050 | 280 | 157500 | 42000 | 199500
b | 0.63 mm thick (24 Gauge) – Galvanized Sheet metal | Sqm. | 230 | 920 | 280 | 211600 | 64400 | 276000
13 | Supply, installation, testing and commissioning of Round Inline fan of following capacities including, supports, canvas connections, motor, stater etc. the fan shall be selected at low noise. Fan shall be installed with five speed fan regulator. |  |  |  |  | - | - | -
a | 500 Cfm @ 15 mm st.pr min. - Fresh Air | Nos | 1 | 7229 | 4500 | 7229 | 4500 | 11729
b | 300 Cfm @ 15 mm st.pr min. - Fresh Air | Nos | 1 | 5639 | 4500 | 5639 | 4500 | 10139
c | 200 Cfm @ 15 mm st.pr min. - Fresh Air | Nos | 3 | 4723 | 4500 | 14169 | 13500 | 27669
d | 150 Cfm @ 15 mm st.pr min. - Fresh Air | Nos | 1 | 4627 | 4500 | 4627 | 4500 | 9127
14 | Supply and installation of Acoustic insulation - Material shall be FM approved, self adhesive, open cell physically crosslinked polyolefin foam. The density of the same shall be within 140-180 Kg/m3.The material should have a thermal conductivity not exceeding 0.041 W/mK. The maximum surface temperature the material should withstand is 105º C and minimum temperature should be -20ºC. The material should conform to Class "O" rating for surface spread of Flame as per BS 476 Part 7. Insulation joints shall be sealed with 3mm thick, 50mm wide OEM recommended self adhesive tape. The Thickness of the insulation material shall be as follows |  |  |  |  | - | - | -
a | 10mm thick | Sqm. | 35 | 980 | 210 | 34300 | 7350 | 41650
15 | Supply & fixing of Thermal Insulation for supply air duct using Closed cell nitrile rubber elastomeric foam insulation along with manufacturer recommended adhesive where the VOC level should not exceed more than 850 grams / Litre. Insulation material manufactured should have fire properties - HB and V0 Rating as per UL 94 |  |  |  |  | - | - | -
a | 13 mm thick (Supply air duct) | Sqm. | 200 | 625 | 200 | 125000 | 40000 | 165000
16 | Supply and installation of Aluminium volume control damper low leakage (low leakage) made out of 1.0mm thick frame and opposed blades of 0.8 mm blade with suitable links, handles, levers and quadrants for manual control of volume of air flow and for proper balancing of air distribution system. Provide engraved type “OPEN & CLOSE” indication. Refer to the drawings for various sizes required. The VCD shall have TDF flanges which suitable to connect with duct. | Sqm. | 2 | 8500 | 1500 | 17000 | 3000 | 20000
17 | Supply and installation of aluminium collar damper, necessary fixing and supporting arrangement for the grilles | Sqm. | 4 | 4950 | 1050 | 19800 | 4200 | 24000
18 | Supply and installation of Extruded Aluminium powder coated fresh air & Exhaust air Louver complete with volume control damper, vermin netting and 45 deg angle suitable for protection against splashing rain water fixed in a powder coated Aluminium angle mount frames. | Sqm. | 3 | 12500 | 1850 | 37500 | 5550 | 43050
19 | Supply, installation, testing and commissioning of tube axial flow type Fire rated Exhaust Air Fan of suitable capacity with powder coated MS/ GSS casing and aluminium alloy impellers with high efficiency aero-foil sections, blades, the impeller directly driven by TEFC induction motor (IE-2) and 'H' class insulation suitable for 3 Phase, 50 Hz, 415±10% Volt, ac supply, (and as per manufacturer specification ) for a static pressure as indicated below. Fan section shall be suitable for Floor Mounted out door application as well as ceiling suspended indoor applications with suitable capacity of starter with Four Pole MCB etc., and other protective devices of approved brands within MS enclosure box complete as required and as per specifications. The fan shall be equipped with mounting bracket Inlet & outlet cone required at discharge. Fans should be AMCA certified. The sound pressure should not exceed 80 db(A) at a distance of 3 Mts. Fan and Motor for Fire exhaust fans shall be suitable for operation at minimum 250 deg C for 2 hrs. The Fan should be complete with all accessories including fire rated canvas connection with metallic flange, vibration isolators, gravity louvers, bird screen etc., as per specification including transportation to site, all mounting arrangements like brackets etc., and cost of all accessories and all labour charges complete. Fan total efficiency should not be less than 60%. Makes:- Crystal Air/Kruger/System Air/ Carry Air/Edgetech/Greenheck/Aerotech
a) | 5500 CFM/ 20mm WC static pressure [canteen exhaust] | Nos. | 1 | 30858 | 8500 | 30858 | 8500 | 39358
b) | 2000 CFM/ 20mm WC static pressure (fresh air) | Nos. | 1 | 22736 | 8500 | 22736 | 8500 | 31236
c) | 1500 CFM/ 20mm WC static pressure (fresh air) | Nos. | 2 | 18560 | 8500 | 37120 | 17000 | 54120
d) | 1200 CFM/ 20mm WC static pressure (fresh air) | Nos. | 2 | 13483 | 8500 | 26966 | 17000 | 43966
e) | 800 CFM/ 20mm WC static pressure (fresh air) | Nos. | 1 | 10121 | 8500 | 10121 | 8500 | 18621
| Total amount for Section-B in INR |  |  |  |  | 11714745 | 1607250 | 13321995

## Fire
FIRE FIGHTING & FIRE HYDRANT SYSTEM
I | COMMON FIRE PUMP ROOM
S. NO | DESCRIPTION | UNIT | QTY | Rate(Rs.) incl.GST | TOTAL AMOUNT(Rs) Incl.GST | Makes
A | FIRE PUMP ROOM EQUIPMENTS
1 | Supplying, installing testing and commissioning of electrical motor driven Main (Hydrant & sprinkler ) Pump of horizontal centrifugal end suction backpull out type with gland packing and capable to deliver 2850LPM (171 m³/ Hr) at 90 MWC with all necessary accessories like bronze impeller, stainless steel shaft along with anti-vibration mounting, coupling, coupling guard and base plate for pump fabricated mild steel channel, foundation bolts and pump should have the dry run sensor provision, etc., as per local fire brigade requirement. The pump shall capable to have 3.5 kg/cm² residual pressure at top most hydrant point. The pump shall be coupled to an electrical motor TEFC, squirrel cage induction motor with speed of 2900 RPM, Electric supply 415V, 50 Hz and complete set shall be mounted on a common base frame. The quoted rate shall includes providing & fixing of coupling, coupling gaurd and Foundation bolts etc. The construction of pump pedestal is under civil scope. | No. | 2 | 415000 | 830000 | KIRLOSKAR
2 | Supplying, installing, testing and commissioning of Diesel Engine driven common stand by pump, horizontal centrifugal end suction backpull out type with gland packing and capable to deliver 2850LPM (171 m³/ Hr) at 90 MWC with all necessary accessories like bronze impeller, stainless steel shaft along with anti-vibration mounting, coupling, gear box, base plate for pump, fabricated mild steel channel with foundation bolts etc., It includes providing and fixing fuel oil tank (capacity as perTAC requirements) with supports and necessary pipe works for diesel engine, battery and battery charger to be connected to control panel of diesel engine and exhaust silencer including necessary pipe work and lagging, pump should have the dry run sensor provision, etc., and shall be automatic in operation with diesel engine control diesel engine control panel with 24V DC storage battery & its battery charger with required Ampere - hour rating, terminal box (2 nos. of 12volts), cooling water line for engine with required pipes / valves / fittings etc., as per TAC including all associated electrical works. The pump shall capable to have 3.5 kg/cm² residual pressure at top most hydrant point. The pump shall coupled to Diesel engine, radiator water cooled type with speed of 1800RPM and complete set shall be mounted on common base frame. Batteries & battery leads with stand, 200 liters capacity Fuel tank ( for 6 Hrs. operation ) with stand & gauge glass, Fuel piping with valves. The quoted rate shall includes radiator water cooling piping(if required) coupling gaurd and other stanadrd accessories and foundation bolts, etc. complete. (the cost for interlock arrangement between main and diesel engine pumps to be included in this item price). The construction of pump pedestal is under civil scope. | No. | 1 | 585000 | 585000 | KIRLOSKAR
3 | Supplying, installing, testing and commissioning of electrical motor driven Jockey pump of vertical multistage inline centrifugal pump capable to deliver 180LPM (10.8 m³/ Hr) at 90 MWC with all necessary accessories like bronze impeller, stainless steel shaft along with anti-vibration mounting pad and flexible connections at discharge end of the pipes, pump should have the dry run sensor provision etc. and shall be automatic in operation.The pump shall be coupled to motor of 15 HP 415V AC 50HZ with speed of 2900RPM and complete set shall be mounted on common base frame. The quoted rate shall includes providing & fixing of coupling, coupling gaurd and Foundation bolts etc. The construction of pump pedestal is under civil scope. | No. | 2 | 90000 | 180000 | KIRLOSKAR
4 | Control Panel for Fire pumps.
A | Fabrication, Supplying, Installation, Testing & Commissioning of electrical control panel, of cubical construction, floor mounted type, fabricated out of 2mm thick CRCA sheet, compartmentalised with hinged lockable doors, dust and vermin proof, powder coated of approved shade after 7 tank treatment process, cable alley, inter-connection, having switchgears and accessories mounting and internal wiring, earth terminals, numbering etc. complete in all respects, suitable for operation on 415 V, 3 phase, 50 HZ. AC supply with enclosure protection class IP 42 as required. | Set | 1 | 380000 | 380000 | DEKARS SLD APPROVED
(i) INCOMER
(a) 2 x 400 Amps. 4 Pole MCCB, 36 KA Thermal Magnetic type with operating handle mechanism and changeover interlocking etc. and necessary accessories (b) Voltmeter (0-500 Volts) with selector switch. (c) Ammeter (0- 400Amps.) with selector switch & CT's etc. (d) Set of 3 Phase indicating lamp. (e) Set of AJ.bus bar Amps.
(ii) OUTGOING.
(a) Hydrant pump. 200 Amps. 4 Pole MCCB, 25 KA Thermal Magnetic type with operating handle mechanism and necessary accessories with 120 HP fully automatic star/ delta starter with over load protection, current sensing type single phase preventor complete with all accessories and internal wiring required for automatic operation, selector switch for local/remote, auto/manual/OFFoperation.
(b) Sprinkler pump. 200 Amps. 4 Pole MCCB, 25 KA Thermal Magnetic type with operating handle mechanism and necessary accessories with 120 HP fully automatic star/ delta starter with over load protection, current sensing type single phase preventor complete with all accessories and internal wiring required for automatic operation, selector switch for local/remote, auto/manual/OFFoperation.
(C) Jockey pump (Hydrant & sprinkler) 2x32 Amps. 4 Pole MCCB, 25 KA Thermal Magnetic type with operating handle mechanism and necessary accessories with 15 HP fully automatic DOL starter with over load protection, current sensing type single phase preventor complete with all accessories and internal wiring required for automatic operation, selector switch for local/remote, auto/manual/OFFoperation.
D) Diesel Engine Control. Control for Diesel Engine comprising:- (i) Auto/Manual selector switch & 3 attempt starting device, timers and relays as required, push buttons, start/stop in manual mode. (ii) Indication lamp for High/Low Lub.oil pressure, High Water Temp.and Engine ON indication. (iii) Battery charger suitable for 12 V/ 24 V DC with boost and tickle selector switch, 0-30 V DC'<volt meter, 0-20A DC Ammeter. (iv) AII standard relays and accessories for automatic operation of diesel engine.
5 | 1100 V GRADE POWER / CONTROL CABLES
| Supplying, laying, testing & commissioning of FRLS, XLPE insulated, PVC outer sheateh, steel armoured, aluminium / copper conductor, 1100v grade power cables with glands etc. The cables shall be laid in tray / Hume pipe / in trenches/on walls/ floor etc. as required. For cables laid out door the rate shall include earth excavation providing brick and sand protection, refilling and compacting the earth.The rate shall excludes tray & Hume pipes.The quoted rate shall includes the end termination for 1.1KV cables with double compression type cable gland and heavy duty tinned copper cable sockets as per the relevant IS standards. Rate shall be inclusive of all sundry materials like adhesive tape , PVC sleeves , bolts and nuts, washers etc. including plugging unused holes. Above 10 mm² shall be aluminium conductor type. |  |  |  |  | HAVELS/ FINCAB/POLYCAB
| a) 3.5 core x 70 sqmm Aluminium conductor cable for Electrical motor Driven hydrant & sprinkler pump. | Mtr | 40 | 1350 | 54000
| a) 3.5 core x 35 sqmm Aluminium conductor cable for Electrical motor Driven water curtain pump. | Mtr | 40 | 800 | 32000
| b) 4 core x 16 sqmm Aluminium conductor cable for Jockey Pump. | Mtr | 40 | 360 | 14400
| c) 12 core x1.5 sqmm for Diesel Engine pump | Mtr | 25 | 450 | 11250
| d) 2 core x 1.5 sqmm for pressure switch | Mtr | 60 | 140 | 8400
| e) 4 core x 2.5 sq mm for MCC to ESP interlocking. | Mtr | 20 | 250 | 5000
6 | CABLE TRAY
| Supplying and fixing of perforated G.I.sheet cable tray with neccessory angle iron suspension supports, anchor fasteners etc. complete. Maximum height of suspension shall not exceed 500 mm.Size of the tray shall be suitable for laying the above mentioned cables. | Rmt | 60 | 2800 | 168000
7 | Supplying, installing testing and commissioning of G.I. Earthing strips of 50mm x 6mm thick, strip shall be run on floor / ceiling / walls, from the equipment to the nearest Earth pit with necessory accessories as required. ( Erath pit shall be executed by other agencies). | Rmt | 100 | 250 | 25000
8 | Supplying, installing, testing and commissioning of G.I Pipes, ERW confirming to IS 1239 Pt - I Heavy grade (Class-C) up to 150mm dia and pipes 200mm dia and above shall be as per IS: 3589 with malleable specials such as Reducers,Tees, elbows, flanges. Including cutting, Welding, fixing in / on walls, ceiling by using suitable supports etc, complete. The exposed pipes shall be protected by one coat of red oxide primer or zinc chromate primer and two coats of synthetic enamel paint of fire red in color shade 536 as per IS 5. The quoted rate shall be exclusive of pipe supports like angle, channel, u-bolt etc. The fittings shall be butt weld type for 65NB and above & socket weld type for 50NB and below. |  |  |  |  | TATA/JINDAL
a | 250mm nominal dia | Rmt | 12 | 4300 | 51600
b | 200mm nominal dia | Rmt | 18 | 3670 | 66060
c | 150mm nominal dia | Rmt | 18 | 3050 | 54900
d | 100mm nominal dia | Rmt | 24 | 1800 | 43200
e | 80mm nominal dia | Rmt | 12 | 1450 | 17400
f | 50mm nominal dia | Rmt | 12 | 750 | 9000
g | 25mm nominal dia | Rmt | 24 | 490 | 11760
9 | Supplying, installing, testing and commissioning of Cast Iron (CI) body Non-return valves as per IS:5312, PN-20 reflux swing check type with required flanges, galvanized nuts & bolts and gaskets etc. complete. |  |  |  | 0
a | 200 mm nominal dia | No. | 3 | 26500 | 79500 | KALPANA/ KARTAR/ UPADHYA/ZOLOTO
c | 80 mm nominal dia | No. | 2 | 10500 | 21000
10 | Supplying, installing testing and commissioning of Cast Iron (C.I) body flanged Y- type Strainer with SS screen 3mm perforations & permanent magnet complete with suitable flanges, galvanized nuts & bolts, gaskets etc. complete.
a | 250mm dia. | No. | 3 | 37800 | 113400
b | 100mm dia. | No. | 2 | 14500 | 29000 | KALPANA/ KARTAR/ UPADHYA/ZOLOTO
11 | Supplying, Installing, testing and commissioning of Cast Iron (C.I) body, flanged Sluice valve as per IS:14846, PN 20 Rating, for suction and delivery side of the pumps and rising spindle (os&y) type with flanges, galvanized bolts & nuts, washers, gaskets etc.
a | 250 mm nominal dia | No. | 3 | 39500 | 118500
b | 200 mm nominal dia | No. | 3 | 26500 | 79500 | KALPANA/ KARTAR/ UPADHYA/ZOLOTO
c | 100mm nominal dia. | No. | 2 | 14500 | 29000
12 | Supplying, Installing, testing and commissioning of Cast Iron (C.I) body Wafer type butterfly valves as per BS 5155, PN-20 rating, slim seal standared lever operated type with required flanges, galvanized nuts & bolts etc. complete.
a | 100mm nominal dia | No. | 1 | 7500 | 7500
b | 50mm nominal dia | No. | 1 | 6500 | 6500
13 | Supplying, installing, testing and commissioning of Gun metal chrome finished Ball valves screwed end type confirming to IS 778 cpmplete with hand lever etc. |  |  |  |  | AUDCO/ INTERVALVE/ ZOLOTO
a | 25 mm nominal dia | No. | 6 | 1100 | 6600
14 | Supply and installation testing and commissioning of differential Pressure switches of suitable range (0 to 16 bar) for pumpsets complete with necessay Ball valves, Fittings like unions / colors / reducers etc.(Standard type for main pump & Differential type for Jockey Pump) | Set | 6 | 3500 | 21000
15 | Supply and installation testing and commissioning of Pressure gauges, bourdon tubetype of suitable range (0-16 bar), 100 mm diameter dial for pumpsets completes with necessary needle valves, siphon, Fittings like unions / colors / reducers etc. | Set | 6 | 1450 | 8700 | ZOLOTO
16 | Supply, fixing, testing and commissioning of air vessel tank shall be fabricated out of of 250 mm dia MS pipe to 1000 mm long complete with 25mm inlet, 25mm drain, 25mm dia connection for air release valve including legs, painting with red oxide primer and finished with fire red enamel paint. It shall be inclusive of all relevant pipes, valves, specials upto pump header and other accessories etc. | No. | 1 | 18500 | 18500
17 | Supplying, installing testing and commissioning of Exhuast pipe for Diesel engine of 100 mm dia M.S. Medium grade with mineral wool insulation with aluminum sheet. The quoted rate shall include 100 mm diameter GI pipe medium grade conforming to IS 1239 Part-1 and mineral wool insulation with aluminum sheeting and Pipe supports also. | Rmt | 30 | 4100 | 123000 | INDFOSS/DANFOSS
18 | supply and fixing of pre-fabricated steel structural materials using MS angle, channel, plate and similar sections for supporting suction & delivery pipe & manifold of fire pump set. The quoted rate shall includes necessary bolt, nut etc. and one coat of promer and synthetic enamal painting of approved shade. | Kg | 500 | 125 | 62500 | H GURU
II | YARD HYDRANT ( EXTERNAL HYDRANT SYSTEM)
1 | Supplying, installing, testing and commissioning of G.I Pipes, ERW confirming to IS 1239 Pt - I Heavy grade (Class-C) up to 150mm dia and pipes 200mm dia and above shall be as per IS: 3589 with malleable specials such as Reducers,Tees, elbows, flanges. Including cutting, Welding, fixing in / on walls, ceiling by using suitable supports etc, complete. The exposed pipes shall be protected by one coat of red oxide primer or zinc chromate primer and two coats of synthetic enamel paint of fire red in color shade 536 as per IS 5. The quoted rate shall be exclusive of pipe supports like angle, channel, u-bolt etc. |  |  |  |  | JINDAL
a | 150mm nominal dia | Rmt | 6700 | 3100 | 20770000
b | 80mm nominal dia | Rmt | 350 | 1450 | 507500
2 | Supplying, installing testing and commissioning of Single headed hydrant valve as per IS 5290 Type A, made of SS with 63 mm dia instantaneous outlet of 80 mm dia fanged inelt ,Blank caps, chain and C.I hand wheels etc complete. | No. | 240 | 6400 | 1536000
3 | 15 M long, 63mm dia RRL hose conforming to IS 636 Type A with SS instantaneous couplings and Hoses shall be stored inside the hose cabinet. | No. | 480 | 6300 | 3024000
4 | Supplying, installing testing and commissioning of SS 63mm dia short branch pipe with 20mm dia diffucer nozzle conforming to IS 903. | No. | 240 | 1900 | 456000 | KALPANA/ KARTAR/ UPADHYA/ZOLOTO
5 | Supplying, installing testing and commissioning of M.S. Hose Box stand/ wall mounted type fabricated out of M.S. sheet of 16 swg. with glass fronted ( 4mm thick glass with rubber beeding) door and size of the cabinet shall be 600mm x 750 mm x 250 mm Quoted rate shall be includes suitable stand for mounting, all fasteners etc, and cabinet shall be powder coated of approved colour both inside and outside. | No. | 240 | 4700 | 1128000
6 | Supplying, installing and commissioning of fire brigade inlet connection of 4 way with each of 63 mm dia. built - in Gun metal instantaneous coupling type with 150 mm dia flanged outlet confirming to IS 5131. Quoted rate shall be included M.S. cabinet of suitable size with mounting supports etc. complete. | No. | 5 | 14500 | 72500
7 | supply and fixing of pre-fabricated steel structural materials using MS angle, channel, plate and similar sections for supporting of above ground hydrant and sprinkler pipes & water curtain pipes (horizontal & vertical) riser. The quoted rate shall includes necessary bolt, nut etc. and one coat of promer and synthetic enamal painting of approved shade. | Kg | 3500 | 125 | 437500
8 | Supplying, Installing, testing and commissioning of valve chambers size of 1000mm x 1000mm | No. | 50 | 14500 | 725000
9 | Supplying, Installing, testing and commissioning of Cast Iron (C.I) body gear type butterfly valves as per BS 5155, PN-20 rating, slim seal standared lever operated type with required flanges, galvanized nuts & bolts etc. complete. |  |  |  |  | AUDCO/ INTERVALVE/ ZOLOTO
a | 150mm nominal dia | No. | 50 | 12500 | 625000
10 | Supplying, Installing, testing and commissioning of Rapping & coating 4mm thickness for below groud piping where as required | RMT | 1 | 650 | 650 | IWL POYCOT
A | WET RISER SYSTEM (INTERNAL HYDRANT SYSTEM) |  |  |  |  | MAKES
1 | Supplying, installing, testing and commissioning of G.I Pipes, ERW confirming to IS 1239 Pt - I Heavy grade (Class-C) up to 150mm dia and pipes 200mm dia and above shall be as per IS: 3589 with malleable specials such as Reducers,Tees, elbows, flanges. Including cutting, Welding, fixing in / on walls, ceiling by using suitable supports etc, complete. The exposed pipes shall be protected by one coat of red oxide primer or zinc chromate primer and two coats of synthetic enamel paint of fire red in color shade 536 as per IS 5. The quoted rate shall be exclusive of pipe supports like angle, channel, u-bolt etc. The fittings shall be butt weld type for 65NB and above & socket weld type for 50NB and below. |  |  |  |  | JINDAL/TATA
a | 150mm nominal dia | Rmt | 1984 | 3100 | 6150400
b | 80mm nominal dia | Rmt | 570 | 1450 | 826500
2 | Supplying, Installing, testing and commissioning of Cast Iron (C.I) body Wafer type butterfly valves as per BS 5155, PN-20 rating, slim seal standared lever operated type with required flanges, galvanized nuts & bolts etc. complete. |  |  |  |  | AUDCO/ INTERVALVE/ ZOLOTO
a | 150mm nominal dia | No. | 53 | 12000 | 636000
3 | Supplying, installing testing and commissioning of Single headed hydrant valve as per IS 5290 Type A, made of SS with 63 mm dia instantaneous outlet of 80 mm dia fanged inelt ,Blank caps, chain and C.I hand wheels etc complete. | No. | 169 | 6500 | 1098500 | NEWAGE/ WINCO/ESSEL
4 | 15 M long, 63mm dia RRL hose conforming to IS 636 Type A with SS instantaneous couplings and Hoses shall be stored inside the hose cabinet. | No. | 338 | 6900 | 2332200 | NEWAGE/ CRC(TYPE B- 4500)/WICO/
5 | Supplying, installing testing and commissioning of SS 63mm dia short branch pipe with 20mm dia diffucer nozzle conforming to IS 903. | No. | 169 | 2000 | 338000 | NEWAGE/ WINCO/ESSEL
6 | Supplying, installing testing and commissioning of M.S. Hose Box stand/ wall mounted type fabricated out of M.S. sheet of 16 swg. with glass fronted ( 4mm thick glass with rubber beeding) door and size of the cabinet shall be 600mm x 750 mm x 250 mm Quoted rate shall be includes suitable stand for mounting, all fasteners etc, and cabinet shall be powder coated of approved colour both inside and outside. | No. | 169 | 4500 | 760500 | FABRICATED
7 | Supplying, installing testing and commissioning of First aid Hose reel drum of 180° swinging type made of MS sheet confirming to IS 884 complete with 19mm dia Rubber braided hose tube of 40m length confirming to IS 444 with gun metal nozzle, control valve & shut off nozzle, complete. | No. | 170 | 7500 | 1275000 | NEWAGE/ WINCO/MONSOR
8 | Supplying, installing and commissioning of fire brigade inlet connection of 4 way with each of 63 mm dia. built - in Gun metal instantaneous coupling type with 150 mm dia flanged outlet confirming to IS 5131. Quoted rate shall be included M.S. cabinet of suitable size with mounting supports etc. complete. | No. | 11 | 12000 | 132000 | NEWAGE/ WINCO/ARMOUR- WITHOUT MS BOX AS ITS CASTED
9 | Supplying and fixing of approved make of 25mm dia automatic air release valve of forged brass single ball type, screwed end complete with unions etc. | No. | 44 | 3300 | 145200 | ZOLOTO/TDK/KARTAR
10 | Supplying, installing, testing and commissioning of Gun metal chrome finished Ball valves screwed end type confirming to IS 778 cpmplete with hand lever etc.
a | 25 mm nominal dia | No. | 190 | 1200 | 228000 | ZOLOTO/KARTAR
11 | supply and fixing of pre-fabricated steel structural materials using MS angle, channel, plate and similar sections for supporting of above ground hydrant and sprinkler pipes & water curtain pipes (horizontal & vertical) riser. The quoted rate shall includes necessary bolt, nut etc. and one coat of promer and synthetic enamal painting of approved shade. | Kg | 5950 | 125 | 743750
B | AUTOMATIC SPRINKLER SYSTEM
1 | Supplying, installing, testing and commissioning of G.I Pipes confirming to IS 1239 Pt - I Heavy grade (Class-C), ERW, above ground pipe with suitable type of supports (Shall be fabricated by M.S. Channel / Angle, anchor fasteners, bolts, nuts, clamps, "U" bolt, malleable specials such as Reducers,Tees, elbows, flanges. Including cutting, Welding, fixing in / on walls, ceiling by using suitable supports etc, . The quoted rate shall also include for chasing / chipping walls, making bore holes in walls whereever required and making them good with filler material. The exposed pipes shall be protected by one coat of red oxide primer or zinc chromate primer and two coats of synthetic enamel paint of fire red in color shade 536 as per IS 5. The fittings shall be butt weld type for 65NB and above & socket weld type for 50NB and below. |  |  |  |  | JINDAL/TATA
a | 150mm nominal dia | Rmt | 1640 | 3100 | 5084000
b | 100mm nominal dia | Rmt | 2380 | 1750 | 4165000
c | 80mm nominal dia | Rmt | 2986 | 1450 | 4329700
d | 65mm nominal dia | Rmt | 3692 | 1050 | 3876600
e | 50mm nominal dia | Rmt | 5590 | 850 | 4751500
f | 40mm nominal dia | Rmt | 4356 | 725 | 3158100
g | 32mm nominal dia | Rmt | 4586 | 625 | 2866250
h | 25mm nominal dia | Rmt | 13160 | 490 | 6448400
2 | Supplying, Installing, testing and commissioning of Cast Iron (C.I) body Wafer type butterfly valves as per BS 5155, PN-20 rating, slim seal standared lever operated type with required flanges, galvanized nuts & bolts etc. complete. |  |  |  |  | AUDCO/ INTERVALVE/ ZOLOTO
a | 150mm nominal dia | No. | 36 | 9500 | 342000
3 | Supplying, Installing, testing and commissioning of Cast Iron (C.I) body Wafer type butterfly valves as per BS 5155, PN-20 rating, slim seal standared lever operated type with required flanges, galvanized nuts & bolts etc. complete. |  |  |  |  | AUDCO/ INTERVALVE/ ZOLOTO
a | 150 mm nominal dia | No. | 36 | 9500 | 342000
4 | Supplying, installing, testing and commissioning of conventional Sprinkler quartzoid bulb of standard coverage & standard respose with 15mm screwed end connection of 68 deg. C. temperature rating, K 80 and orifice shall not be less than 12.7mm. Sprinklers shall be UL Listed / FM approved with Chrome finished. |  |  |  |  | NEWAGE/ HD FIRE/TYCO
a | Pendent sprinkler | No. | 11300 | 410 | 4633000
5 | Supplying, installing, testing and commissioning of flanged hydralically operated Sprinkler alarm control valve complete with water motor gong bell, basic trims as required, pressure gauges, pressure switch, drain valves, ball valves etc. complete. Alarm valve shall be UL Listed / FM approved. |  |  |  |  | NEWAGE/ HD FIRE
a | 150mm dia. | No. | 7 | 85000 | 595000
6 | Supplying, installing, testing and commissioning of flow switch (water flow detector) , Flow switch shall have a paddle made of flexible material of the widthto fit within the pipe bore. The terminal box shall be mounted over the paddle/ pipe through a connecting socket.The switch shall be potential free in either NO or NC position as required. The switch shall be able to trip and make/ break contact on the operation of a sprinkler head. The terminal box shall have connections for wiring to the Fire alarm panel. The seat shall be of stainless steel. The flow switch shall have IP: 55 protection. |  |  |  |  | HONEYWELL/ SS
a | 150 mm nominal dia | No. | 40 | 5500 | 220000
7 | Supplying and fixing of approved make of 25mm dia automatic air release valve of forged brass single ball type, screwed end complete with unions etc. | No. | 52 | 2500 | 130000 | ZOLOTO
8 | Supplying, installing, testing and commissioning of Gun metal chrome finished Ball valves screwed end type confirming to IS 778 cpmplete with hand lever etc. |  |  |  |  | ZOLOTO
a | 50mm dia.(Drain connection) | No. | 40 | 5500 | 220000
b | 25 mm dia. | No. | 40 | 1450 | 58000
C | ADDRESSABLE FIRE DETECTION AND ALARM SYSTEM
1 | Addressable intelligent 6- Loop Fire Alarm Control panel with voice evaucaution system with 48 hours battery back up in standby and 30 minuts in alarm condition and battery charger. The panel shall consisting with 80 character LCD display, Network card and RS 485 for networking. 125 detectors & 125 devices for each loop. |  |  |  |  | APOLLO/ NOTIFIER/
| 8-LOOP | No | 1 | 480000 | 480000
| 6-LOOP | No | 2 | 430000 | 860000
| 5-LOOP | No | 1 | 410000 | 410000
| 4-LOOP | No | 4 | 350000 | 1400000
| 2-LOOP | No | 1 | 290000 | 290000
| 1-LOOP | No | 4 | 135000 | 540000
2 | Supplying, installing, testing and commissioning of Addressable Manual Call Point with back box. | No | 96 | 5500 | 528000 | APOLLO/ NOTIFIER/
3 | Supplying, installing, testing and commissioning of Analogue Addressable sounder with strobe | No | 96 | 5500 | 528000 | APOLLO/ NOTIFIER/
4 | Supplying, installing, testing and commissioning of addressable photo electric smoke detector (optical) with base, junction box and other accessories (true ceiling & above false ceiling) | No | 4464 | 3500 | 15624000 | APOLLO/ NOTIFIER
5 | Supplying, installing, testing and commissioning of rate of rise heat detector with base, junction box and other accessories. | No | 200 | 3500 | 700000 | APOLLO/ NOTIFIER/SECRITON
6 | Analogue Addressable Fault isolator module capable of monitoring shorted loop circuit and automatically restore communications when shorted conditions are corrected | No | 236 | 4200 | 991200 | APOLLO/ NOTIFIER/SECRITON
7 | Supplying, installing, testing and commissioning of Analogue Addressable Monitor Module (single input module) for integrating Sprinkler flow switch in all floors with FACP at ground floor. | No | 44 | 4500 | 198000 | APOLLO/ NOTIFIER/SECRITON
8 | Supplying, installing, testing and commissioning of beam detectors 100m range x 15 m width | No | 78 | 90000 | 7020000 | system sensor/notifier/apollo
9 | Supplying, installing, testing and commissioning of 2C x 1.5 mm², armoured, single stand, outer sheathed, FRLS, PVC insulated copper conductor cable confirming to specified IS standards . | Rmt | 37700 | 140 | 5278000 | POLYCAB/FINECAB/HAVELLS
D | FIRE EXTINGUISHERS
1 | Supplying, installing and commissioning of Portable Fire extinguishers of following type & capacity. |  |  |  |  | KANEX/ NITIN/ SAFEX
a | Carbon-di- oxide type fire extinguisher of 4.5 kgs. Capacity, CO2 gas as per IS 15222 with controll discharge mechanism fitted with Hose & Horn applicable on Class B fire rating 21B confirming to IS: 15683 and the cylinder must carry ISI mark. | No | 191 | 7500 | 1432500
b | Carbon-di- oxide type fire extinguisher of 9.0 kgs. Capacity, CO2 gas as per IS 15222 with controll discharge mechanism fitted with Hose & Horn applicable on Class B fire rating 21B with trolly confirming to IS: 15683 and the cylinder must carry ISI mark. | No | 66 | 12500 | 825000
c | ABC powder type fire extinguisher of 6 Kgs. Capacity, with initial filling (Mono Ammonium Phospate Powder 90) in brand new cylinder with powder coated finish, Stored Pressur type, Pressure Gauge, Controllable discharge mechanism with Hose & Nozzle , confirming to IS:15683 and the cylinder must carry ISI mark. (ABC Dry Chemical Powder- MAP 90%) | No | 263 | 3700 | 973100
d | DCP powder type fire extinguisher of 25 Kgs. Capacity, with initial filling (Mono Ammonium Phospate Powder 90) in brand new cylinder with powder coated finish, Stored Pressur type, Pressure Gauge, Controllable discharge mechanism with Hose & Nozzle , confirming to IS:15683 and the cylinder must carry ISI mark. (ABC Dry Chemical Powder- MAP 90%) | No | 63 | 10500 | 661500
e | Mechanical Foam type fire extinguisher 9Lts. Capacity, with initial filling in brand new cylinder with powder coated finish, fitted with Gun metal union, high pressure CO2 gas cartridge, hose and ABS type branch pipe and wall mounting bracket etc. complete, confirming to IS: 15683:2008. The cylinder must carry ISI mark. | No. | 125 | 4500 | 562500
f | Fire buckets round bottom type enamel painted, white inside & Red out side and Letter "FIRE" in black out side and handle with mounting bracket. | Nos. | 67 | 650 | 43550
g | Fire bucket stand fabricated by MS angles to install 4 Nos. of buckets | Nos. | 67 | 2500 | 167500
|  |  |  | TOTAL | 127951770
19192765.5

## Plumbing
WATER SUPPLY, SANITARY,GAS PIPE LINE,WATER COOLERS,WTP,STP,RO,PUMPS
S.No. | Description of Work | Unit | Quantity | Rate(Rs.) incl.GST | Amount (in Rs.) Incl.GST
1 | Supplying, laying & testing UPVC pipes line conforming to ASTMD2467, and schedule so conforming to IS 4985-2000 class 5PN (supreme, ashirvad, prince)
a) | Dia 15mm | Rmt | 870 | 211 | 183570
b) | Dia 20mm | Rmt | 76 | 326 | 24776
c) | Dia 25mm | Rmt | 229 | 538 | 123202
d) | Dia 32mm | Rmt | 723 | 806 | 582738
e) | Dia 40mm | Rmt | 238 | 1254 | 298452
f) | Dia 50mm | Rmt | 80 | 1855 | 148400
g) | Dia 65mm | Rmt | 15 | 2649 | 39735
2 | Supplying, fixing ,testing & commissioning of EWC | NOS. | 235 | 3200 | 752000
3 | Supplying, fixing ,testing & commissioning of IWC (Orissa pan) of size 53cmx41cmx28.5cm | NOS. | 25 | 1632 | 40800
4 | Supply & fixing bib cock cum health faucet | NOS. | 260 | 1020 | 265200
5 | Supplying and fixing Indian make Flat Back Wash Hand Basin | NOS. | 300 | 1100 | 330000
6 | Supplying, fixing ,testing & commissioning of pillar cock | NOS. | 300 | 840 | 252000
7 | Supplying, fixing & testing of bottle trap with 300mmx125mm long connecting pipe | No's | 300 | 1060 | 318000
8 | Supplying, fixing & testing of waste coupling 32mm full thread | No's | 300 | 440 | 132000
9 | Supplying,testing of urinals with size 355x345x535 fixing accessories | No's | 160 | 3280 | 524800
10 | Supplying,fixing of AUTOCLOSING concealed urinals flush valve | No's | 160 | 2280 | 364800
11 | Supplying and fixing of division plate for urinals | No's | 160 | 1680 | 268800
12 | Supplying and fixing bib taps of size 12.70mm dia of Indian make heavy duty (short body) | No's | 160 | 776 | 124160
13 | Supplying and fixing of stainless steel sink of size 37'LX18'WX9'D | No's | 10 | 7832 | 78320
14 | Supplying and fixing soap dish heavy type of approved make ISI quality with NP screws etc. | No's | 200 | 608 | 121600
15 | Supplying and fixing TV shape mirror with plastic frame of size 609.6mm x 457.2mm , plywood back with NP screws 1st quality including cost and conveyance of all materials, labour charges , overheads & contractors profit for finished item of work in all floors. | No's | 300 | 640 | 192000
16 | Supplying and fixing of 25.4mm dia , 609.6mm long aluminium anodized towel rods with brackets | No's | 250 | 1096 | 274000
17 | Supplying and fixing steel surgical long elbow action handle long bib cock as approved | No's | 40 | 940 | 37600
18 | Supplying and fixing steel surgical long elbow action handle short dia bib cock | No's | 60 | 700 | 42000
19 | Supply & fixing shower with shower arm and wall flange heavy | No's | 30 | 684 | 20520
20 | Supply & fixing of angle cock with trangular handle | No's | 700 | 684 | 478800
21 | Supply & fixing of floor trap 110mm | No's | 950 | 200 | 190000
22 | Supplying and fixing gully trap heavy type of approved make ISI quality etc. | No's | 468 | 610 | 285480
23 | Supplying and fixing of HDPE pipes conforming IS4984 PE1000 & SDR 21(supreme,kelvin,LHP) |  |  |  | 0
a) | 160mm dia | RM | 1790 | 134 | 239860
b) | 200mm dia | RM | 465 | 176 | 81840
c) | 250mm dia | RM | 12 | 218 | 2616
d) | 110mm dia | RM | 1777 | 422 | 749894
e) | 75mm dia | RM | 1040 | 196 | 203840
f) | 50mm dia | RM | 175 | 88 | 15400
24 | Supplying, fixing ,testing & commissioning of manhole |  |  |  | 0
a) | 1290mm long | No's | 22 | 51090 | 1123980
b) | 1490mm long | No's | 25 | 62305 | 1557625
c) | 1590mm long | No's | 24 | 67511 | 1620264
d) | 1160mm long | No's | 25 | 62756 | 1568900
e) | 1500mm long | No's | 26 | 78984 | 2053584
25 | Supplying and fixing ball valve |  |  |  | 0
a) | Dia 50mm | No's | 2 | 578 | 1156
b) | Dia 25mm | No's | 48 | 200 | 9600
c) | Dia 65mm | No's | 1 | 680 | 680
d) | Dia 40mm | No's | 22 | 374 | 8228
e) | Dia 32mm | No's | 40 | 308 | 12320
f) | Dia 20mm | No's | 28 | 130 | 3640
26 | Supply and fixing in position Non-Return Valves with matching companion fittings complete etc. |  |  |  | 0
a) | Dia 32mm | No's | 2 | 2510 | 5020
b) | Dia 40mm | No's | 10 | 4182 | 41820
27 | Supply ,laying and testing of LPG Manifold sout east coner to bus body block 1 & 2 by means of 50mm 'C' class MS pipe confirm to IS Code 1239 part 1 and also connecting different point by 15 MS 'C' class pipe |  |  |  | 0
a) | M.S pipe 50mm 'C' class | mtr | 900 | 880 | 792000
b) | M.S pipe 15mm 'C' class | mtr | 30 | 200 | 6000
28 | 500 LPH R O , manual with storage tank of 500 ltrs in Stainless Steel with UV stream (1 for kitech & dining & other admin block). | sets | 2 | 132000 | 264000
29 | 80 KLD STP System & Process Design, Detailed Engineering, Supply of Equipment, Interconnecting Piping, Erection and Commissioning of the Plant as per Cyrus Water Technologies Pvt. Ltd. Proposal. | No's | 1 | 4800000 | 4800000
30 | Design, Engineering, Excluding tanks from our scope of Supply and Supervision Erection & Commissioning of 15M 3 /Hr 400 KLD WTP Water Treatment Plant. | No's | 1 | 1220000 | 1220000
31 | Supply installation testing commisioning of hydronumatic pumps having a discharge of 70 m/cum per hour 45 meters head with 500 litres pressure tank | No's | 2 | 864160 | 1728320
32 | Supply installation testing commitioning of water coolers 80 litres storage capacity 40 litres cooling capacity with two taps | No's | 25 | 28000 | 700000
|  | TOTAL |  |  | 25304340

## Electrical (2)
INTERNAL & EXTERNAL ELECTRIFICATION WORKS
S.No | DESCRIPTION | UNIT | Total Qty. | Rate (Rs) Incl.GST |  | Amount (in Rs.) Incl.GST
|  |  |  | Supply | Erection | Supply | Erection | Total
I) | INTERNAL ELECTRICALS
1) | Internal Wiring
a) | Point Wiring for Light/ Fan/ exhaust fan with 2 runs of 1100V grade 1.5 Sq.mm & 1 run of 1.5 Sq.mm PVC insulated multistrand , FRLS , Copper conductor wires , run in and including 25mm dia heavy gauge PVC conduits concealed in wall / ceiling conforming to IS 732 including all accessories such as junction boxes, conduit bends elbows and anodised GI Switch box with modular switch and the box covered with front plate including connections to Earth terminal.
i) | One Light point controlled by one 6 A switch. | No | 580 | 885 | 120 | 513300 | 69600 | 582900
ii) | Two Light point controlled by one 6 A switch. | No | 415 | 1100 | 120 | 456500 | 49800 | 506300
iii) | Ceiling fan point controlled by one 6 A switch and electronic fan regulator of 100 W step type with concealed MS fan hook box | No | 356 | 1250 | 120 | 445000 | 42720 | 487720
iv) | Exhaust fan point controlled by one 6 A switch. | No | 80 | 950 | 120 | 76000 | 9600 | 85600
v) | Call bell point controlled by one 6 A Bell push switch and Buzzer | No | 16 | 850 | 120 | 13600 | 1920 | 15520
2) | Supply and Wiring with the following size 1100V grade PVC insulated multistrand FRLS Copper conductor wires in and including suitable size heavy gauge PVC conduit concealed in wall / Ceiling including all accessories such as junction boxes, bends, elbows including end terminated with suitable lugs.
a) | 2 runs of 2.5 Sq.mm wires with 1run of 2.5 Sq.mm wire in and including 25 mm Dia PVC Conduit (For Lighting Circuit ) | Rmt | 5000 | 280 | 50 | 1400000 | 250000 | 1650000
b) | 2 runs of 4 Sq.mm wires with 1run of 4 Sq.mm wire in and including 25 mm Dia PVC Conduit (For Power Circuit ) | Rmt | 6600 | 280 | 50 | 1848000 | 330000 | 2178000
c) | 2 runs of 6 Sq.mm wires with 1run of 6 Sq.mm wire in and including 25 mm Dia PVC Conduit (For AC Circuit ) | Rmt | 1700 | 280 | 50 | 476000 | 85000 | 561000
d) | 4 runs of 6 Sq.mm wires with 2run of 6 Sq.mm wire in and including 32 mm Dia PVC Conduit (For Lighting DB ) | Rmt | 400 | 560 | 50 | 224000 | 20000 | 244000
e) | 4 runs of 10 Sq.mm wires with 2run of 10 Sq.mm wire in and including 32 mm Dia PVC Conduit (For Power DB ) | Rmt | 400 | 560 | 50 | 224000 | 20000 | 244000
f) | Wiring with 3Cx2.5 sq.mm PVC insulated copper cable in 25mm dia 16 swg thick MS surface Conduit with ceiling rose directly connected to existing MCB DB including cutting, chiseling and chipping the wall/flooring, masonry work including the painting of the wall or wherever the required & the finishing is matched with existing finishing with all labour charges etc., complete for light, and exhaust fan points in respective areas
i | Three Light Points Controlled by one 10A SPMCB | No | 700 | 1150 | 280 | 805000 | 196000 | 1001000
ii | Four Light Points Controlled by one 10A SPMCB | No | 360 | 1380 | 310 | 496800 | 111600 | 608400
iii | Five Light Points Controlled by one 10A SPMCB | No | 400 | 1450 | 350 | 580000 | 140000 | 720000
3) | Supply and Fixing of 6A 3pin modular plug socket and 6 A modular switch control duly recessed in wall with concealed anodized metal box and cover frame including circuit wiring of 2x2.5+1x1.5 sq.mm multistrand copper conductor cable from DB & connections including supply and laying of 16SWG 25mm Dia MS conduit on ceiling/on wall and alsoincluding all labour charges etc.,complete. (Make : ANCHOR WOODS, LEGRAND MOSIAC, MK) | No | 590 | 490 | 150 | 289100 | 88500 | 377600
4) | Supply and Fixing of 6/16A 5pin modular plug socket and 16 A modular switch control duly recessed in wall with concealed anodized metal box and cover frame etc.,complete. (Make : ANCHOR WOODS, LEGRAND MOSIAC, MK) | No | 855 | 680 | 150 | 581400 | 128250 | 709650
5) | Supply and fixing 20A, 240V, SPN industrial type socket outlet, with 2pole and earth, metal enclosed plug top along with 20/32A, 'C' curve, SP MCB in sheet steel enclosure, on surface on in recesses, with chain metal cover for the socket outlet and complete with connections, testing and commissioning etc as required etc.,complete. (Make : ANCHOR WOODS, LEGRAND MOSIAC, MK) | No | 74 | 2124 | 200 | 157176 | 14800 | 171976
6) | Supply and Fixing with combination of 2nos 6/16A 5pin modular plug socket and 2nos 16 A modular switch control duly recessed in wall with concealed anodized metal box and cover frame including earth connections and all labour charges etc.,complete. | No | 204 | 1080 | 280 | 220320 | 57120 | 277440
7) | Supply and fixing 16A, 240V, SPN industrial type socket outlet, with 2pole and earth, metal enclosed plug top along with 20/32A, 'C' curve, SP MCB in sheet steel enclosure, on surface on in recesses, with chain metal cover for the socket outlet and complete with connections, testing and commissioning etc as required etc.,complete. (Make : ANCHOR WOODS, LEGRAND MOSIAC, MK) | No | 570 | 2124 | 236 | 1210680 | 134520 | 1345200
8) | Supply and fixing 32A, 440V, TPN industrial type socket outlet, with 4pole and earth, metal enclosed plug top along with 20/32A, 'C' curve, TP MCB in sheet steel enclosure, on surface on in recesses, with chain metal cover for the socket outlet and complete with connections, testing and commissioning etc as required etc.,complete. (Make : ANCHOR WOODS, LEGRAND MOSIAC, MK) | No | 300 | 3304 | 354 | 991200 | 106200 | 1097400
9 | Circuit wiring | [6 empty] | 0
a) | Wiring for mains along with earth wire with the 4Rx10 Sq.mm +2Rx10 sq.mm F.R. P.V.C insulated flexible copper conductor, single core cable in surface/recessed 32 mm dia 16SWG MS Conduit as required | Rmt | 7000 | 708 | 94 | 4956000 | 658000 | 5614000
b) | Wiring for mains along with earth wire with the 4Rx6 Sq.mm +2Rx6 sq.mm F.R. P.V.C insulated flexible copper conductor, single core cable in surface/recessed 32 mm Dia 16SWG MS conduit as required | Rmt | 12250 | 330 | 59 | 4042500 | 722750 | 4765250
c) | Wiring for Lighting Circuit mains along with earth wire with the 2Rx2.5 Sq.mm +1Rx2.5 sq.mm F.R. P.V.C insulated flexible copper conductor, single core cable in and including surface/recessed 25 mm Dia 16SWG MS conduit as required | Rmt | 78400 | 170 | 30 | 13328000 | 2352000 | 15680000
d) | Wiring for Power Circuit mains along with earth wire with the 2Rx4 Sq.mm +1Rx4 sq.mm F.R. P.V.C insulated flexible copper conductor, single core cable in and including surface/recessed 25 mm Dia 16SWG MS conduit as required. For 6/16A Power Sockets & Geyser | Rmt | 34000 | 230 | 40 | 7820000 | 1360000 | 9180000
e) | Wiring for AC Circuit mains along with earth wire with the 2Rx6 Sq.mm +1Rx6 sq.mm F.R. P.V.C insulated flexible copper conductor, single core cable in and including surface/recessed 25 mm Dia 16SWG MS conduit as required. For 20A AC Power Sockets | Rmt | 2100 | 280 | 80 | 588000 | 168000 | 756000
10) | DISTRIBUTION BOARDS
b) | Supply and fixing 12 way TPN Factory made Distribution board with IP-42 protection ( Metal Door ) suitable for 3 phase 4P MCB as incomer ans 10 kA SP MCBs as outgoing including internal connection and labour charges for surface/ flush mounting etc.,complete.
i) | 63A FP MCB - 1no for Incomer, 10kA 6-20A SP MCBs – 36Nos for outgoing.( PDB) | Nos | 16 | 16500 | 2124 | 264000 | 33984 | 297984
c) | Supply and fixing 12 way TPN Factory made Distribution board with IP-42 protection ( Metal Door ) suitable for 3 phase 4P MCB as incomer ans 10 kA SP MCBs as outgoing including internal connection and labour charges for surface/ flush mounting etc.,complete.
i) | 40A FP MCB - 1no for Incomer, 10kA 6-20A SP MCBs – 36Nos for outgoing.( LDB) | Nos | 16 | 16500 | 2124 | 264000 | 33984 | 297984
d) | Supply and fixing 8 way TPN Factory made Distribution board with IP-42 protection ( Metal Door ) suitable for 3 phase 4P MCB as incomer ans 10 kA SP MCBs as outgoing including internal connection and labour charges for surface/ flush mounting etc.,complete.
i) | 63A FP MCB - 1no for Incomer, 10kA 6-20A SP MCBs – 24Nos for outgoing.( PDB) | Nos | 16 | 12500 | 2124 | 200000 | 33984 | 233984
e) | Supply and fixing 8 way TPN Factory made Distribution board with IP-42 protection (acrylic Door ) suitable for 3 phase 4P MCB as incomer ans 10 kA SP MCBs as outgoing including internal connection and labour charges for surface/ flush mounting etc.,complete
f) | Supply and fixing 32/40, 3Ph, 5Pin industrial type socket outlet, with TP+N+ and earth, metal enclosed plug top along with 32/40A, 'C' curve, 4p MCB in sheet steel enclosure, on surface on in recesses, with chain metal cover for the socket outlet and complete with connections, testing and commissioning etc as required. | Nos | 70 | 5900 | 590 | 413000 | 41300 | 454300
g) | Supply and fixing of Three phase Factory made 100A, 4P MCB with MS enclosure including internal connection and labor charges for surface/ flush mounting etc.,complete as finished of item.. | Nos | 70 | 7670 | 590 | 536900 | 41300 | 578200
h) | Supply and fixing 4 Way VTPN - Vertical type Distribution board with IP -43 Protection with 125A, 4 Pole 25 kA MCCB as incomer with 4 Nos 63A TP MCBs as outgoing including internal connection and labour charges for flush mounting etc. Make: Legrand / Scnieder for Lighting Distribution | Nos | 16 | 32500 | 1770 | 520000 | 28320 | 548320
i) | Supply and fixing 4 Way VTPN - Vertical type Distribution board with IP -43 Protection with 125A, 4 Pole 25 kA MCCB as incomer with 4Nos 63A TP MCBs as outgoing including internal connection and labour charges for flush mounting etc. Make: Legrand / Scnieder for Power Distribution | Nos | 16 | 32500 | 1770 | 520000 | 28320 | 548320
j) | Supply and fixing 8 Way VTPN - Vertical type Distribution board with IP -43 Protection with 125A, 4 Pole 25 kA MCCB as incomer with 8 Nos 40A TP MCBs as outgoing including internal connection and labour charges for flush mounting etc. Make: Legrand / Scnieder for Lighting Distribution | Nos | 10 | 42500 | 1500 | 425000 | 15000 | 440000
k) | Supply and fixing 8 Way VTPN - Vertical type Distribution board with IP -43 Protection with 125A, 4 Pole 25 kA MCCB as incomer with 8 Nos 63A TP MCBs as outgoing including internal connection and labour charges for flush mounting etc. Make: Legrand / Scnieder for Power Distribution | Nos | 8 | 42500 | 1500 | 340000 | 12000 | 352000
l) | Supply and fixing 12 Way VTPN - Vertical type Distribution board with IP -43 Protection with 125A, 4 Pole 25 kA MCCB as incomer with 12 Nos 40A TP MCBs as outgoing including internal connection and labour charges for flush mounting etc. Make: Legrand / Scnieder for Lighting Distribution | Nos | 56 | 63000 | 1500 | 3528000 | 84000 | 3612000
m) | Supply and fixing 12 Way VTPN - Vertical type Distribution board with IP -43 Protection with 125A, 4 Pole 25 kA MCCB as incomer with 12 Nos 63A TP MCBs as outgoing including internal connection and labour charges for flush mounting etc. Make: Legrand / Scnieder for Power Distribution | Nos | 8 | 68000 | 1500 | 544000 | 12000 | 556000
II | M.V PANELs
5.1 | Sub-Panel 1 (consists of) Incomer 415V, 1250A, 4P, ACB with (O/C+S/C+E/F+SPP Releases) with all protections & thermal based releases and all other accessories-1No LED Type Phase Indicating Lamps (R,Y,B) – 1set 6A SP MCB – 3Nos 1250A/5A, Cl.1.0, 15VA Tape wound Cts – 3Nos 0-1250A Digital type Ammeter with selector switch – 1set 0-500V Digital type voltmeter with selector switch - 1set Load Manger – 1no Outgoing Feeders 400A , 50KA , TPN MCCB- 5Nos (Each feeder consisting of) 400A, TPN, 50KA MCCB with (O/C+S/C+E/F+SPP Releases) with all protections & thermal based releases and all other accessories-1No 100A - 3Nos (Each feeder consisting of) 100A, TPN, 25KA MCCB with (O/C+S/C+E/F+SPP Releases) with all protections & thermal based releases and all other accessories-1No 1250A, 3Ph, 4wire, 50Hz, 50KA, ELectrical grade aluminium busbars- 1set | No | 5 | 550000 | 18500 | 2750000 | 92500 | 2842500
5.2 | Sub-Panel 2 (consists of) Incomer 415V, 1250A, 4P, ACB with (O/C+S/C+E/F+SPP Releases) with all protections & thermal based releases and all other accessories-1No 6A SP MCB – 3Nos LED Type Phase Indicating Lamps (R,Y,B) – 1set 1250A/5A, Cl.1.0, 15VA Tape wound Cts – 3Nos 0-1250A Digital type Ammeter with selector switch – 1set 0-500V Digital type voltmeter with selector switch - 1set Load Manger – 1no Outgoing Feeders 400A , 50KA , TPN MCCB- 5Nos (Each feeder consisting of) 400A, TPN, 50KA MCCB with (O/C+S/C+E/F+SPP Releases) with all protections & thermal based releases and all other accessories-1No 100A - 3Nos (Each feeder consisting of) 100A, TPN, 25KA MCCB with (O/C+S/C+E/F+SPP Releases) with all protections & thermal based releases and all other accessories-1No 1250A, 3Ph, 4wire, 50Hz, 50KA, ELectrical grade aluminium busbars- 1set | No | 5 | 550000 | 18500 | 2750000 | 92500 | 2842500
5.3 | Sub-Panel 3 (consists of) Incomer 415V, 1250A, 4P, ACB with (O/C+S/C+E/F+SPP Releases) with all protections & thermal based releases and all other accessories-1No 6A SP MCB – 3Nos LED Type Phase Indicating Lamps (R,Y,B) – 1set 1250A/5A, Cl.1.0, 15VA Tape wound Cts – 3Nos 0-1250A Digital type Ammeter with selector switch – 1set 0-500V Digital type voltmeter with selector switch - 1set Load Manger – 1no Outgoing Feeders 400A , 50KA , TPN MCCB- 5Nos (Each feeder consisting of) 400A, TPN, 50KA MCCB with (O/C+S/C+E/F+SPP Releases) with all protections & thermal based releases and all other accessories-1No 100A - 3Nos (Each feeder consisting of) 100A, TPN, 25KA MCCB with (O/C+S/C+E/F+SPP Releases) with all protections & thermal based releases and all other accessories-1No 1250A, 3Ph, 4wire, 50Hz, 50KA, ELectrical grade aluminium busbars- 1set | No | 5 | 550000 | 18500 | 2750000 | 92500 | 2842500
5.4 | Sub-Panel 4 (consists of) Incomer 415V, 1250A, 4P, ACB with (O/C+S/C+E/F+SPP Releases) with all protections & thermal based releases and all other accessories-1No 6A SP MCB – 3Nos LED Type Phase Indicating Lamps (R,Y,B) – 1set 1250A/5A, Cl.1.0, 15VA Tape wound Cts – 3Nos 0-1250A Digital type Ammeter with selector switch – 1set 0-500V Digital type voltmeter with selector switch - 1set Load Manger – 1no Outgoing Feeders 400A , 50KA , TPN MCCB- 5Nos (Each feeder consisting of) 400A, TPN, 50KA MCCB with (O/C+S/C+E/F+SPP Releases) with all protections & thermal based releases and all other accessories-1No 100A - 3Nos (Each feeder consisting of) 100A, TPN, 25KA MCCB with (O/C+S/C+E/F+SPP Releases) with all protections & thermal based releases and all other accessories-1No 1250A, 3Ph, 4wire, 50Hz, 50KA, ELectrical grade aluminium busbars- 1set | No | 5 | 550000 | 18500 | 2750000 | 92500 | 2842500
5.5 | Sub-Panel 5 (consists of) Incomer 415V, 1250A, 4P, ACB with (O/C+S/C+E/F+SPP Releases) with all protections & thermal based releases and all other accessories-1No 6A SP MCB – 3Nos LED Type Phase Indicating Lamps (R,Y,B) – 1set 1250A/5A, Cl.1.0, 15VA Tape wound Cts – 3Nos 0-1250A Digital type Ammeter with selector switch – 1set 0-500V Digital type voltmeter with selector switch - 1set Load Manger – 1no Outgoing Feeders 400A , 50KA , TPN MCCB- 5Nos (Each feeder consisting of) 400A, TPN, 50KA MCCB with (O/C+S/C+E/F+SPP Releases) with all protections & thermal based releases and all other accessories-1No 100A - 3Nos (Each feeder consisting of) 100A, TPN, 25KA MCCB with (O/C+S/C+E/F+SPP Releases) with all protections & thermal based releases and all other accessories-1No 1250A, 3Ph, 4wire, 50Hz, 50KA, ELectrical grade aluminium busbars- 1set | No | 5 | 550000 | 18500 | 2750000 | 92500 | 2842500
III | EARTHING
a) | Supply and providing earth electrode with 600 x 600 x 3.15 copper plate electrode enclosed in cement concrete chamber of size 400x 400 x 400mm and 300 x 300mm size cast iron cover with cast iron frame embedded in cement mortar to be provided on the top of the masonry chamber, use of salt, coat or coke as required for earthing media, providing 50mm diameter GI pipe with standard type GI funnel arrangement at top and all complete as per IS: 3043 - 1987 | Nos | 16 | 11800 | 1770 | 188800 | 28320 | 217120
b) | Suppy,Installation of 40 mm dia GI Earthpipe of 3 mtr length Earth Station including excavation,back filling and construction of earth chamber.The scope includes civil work like excavation,back filling and construction of chamber with cast iron cover of size 300 x 300 MM and providing charcoal, salt and sand for the earth pit as per IS 3043. | Nos | 96 | 5900 | 1888 | 566400 | 181248 | 747648
c) | Supply and fixing of following earth strips/ conductors. The scope includes supply and fixing of copper lugs wherever found necessary, brass bolts, nuts and washers for fixing arrangement etc., (from earth station to main panel).
i) | 50 x 6 MM G.I. Flat | Rmt | 4600 | 350 | 24 | 1610000 | 110400 | 1720400
i) | 25 x 6 MM G.I. Flat | Rmt | 4000 | 180 | 15 | 720000 | 60000 | 780000
i) | 75 x 10 MM COPPER Flat | Rmt | 120 | 3776 | 15 | 453120 | 1800 | 454920
ii) | 8 SWG G.I.Wire | Rmt | 10300 | 20 | 5 | 206000 | 51500 | 257500
i) | 75 x 10 MM G.I. Flat | Rmt | 800 | 413 | 20 | 330400 | 16000 | 346400
IV | MISCELLANEOUS
a) | Providing, lying and fixing of 50mm dia medium class GI pipe in ground complete with fitting including trenching (75cm deep) and re-filling etc as required | Mtr | 160 | 600 | 60 | 96000 | 9600 | 105600
b) | 600mm wide Overhead GI perforated cable tray with top cover & necessary angles supports clamps etc for fixing on wall/columns at required height from FFL including labour chages etc | Mtr | 2430 | 2500 | 177 | 6075000 | 430110 | 6505110
c) | 450mm wide Overhead GI perforated cable tray with top cover & necessary angles supports clamps etc for fixing on wall/columns at required height from FFL including labour chages etc | Mtr | 1850 | 2000 | 150 | 3700000 | 277500 | 3977500
d) | 300mm wide Overhead GI perforated cable tray with top cover & necessary angles supports clamps etc for fixing on wall/columns at required height from FFL including labour chages etc | Mtr | 2220 | 1800 | 150 | 3996000 | 333000 | 4329000
e) | 150mm wide Overhead GI perforated cable tray with top cover & necessary angles supports clamps etc for fixing on wall/columns at required height from FFL including labour chages etc | Mtr | 1200 | 900 | 120 | 1440000 | 144000 | 1584000
f) | 200mm wide x 38mm height heavy gauge G.I floor race way with top cover & suitable size junction box , cutting with existing VDF floor embedded in flooring and flushed with existing flooring including labor charges etc… The Junction Box cover shall be Stainless steel material .( Heavy Gauge ) | Mtr | 800 | 1000 | 100 | 800000 | 80000 | 880000
V | SUPPLY & FIXING OF FIXTURES
1 | SUPPLY & FIXING OF FIXTURES
a) | 210W LED light fixtures (BY415P LED275S CW PSU GR FG WB XTFCL V1 of Philips make or equivalent) | No | 3370 | 11600 | 800 | 39092000 | 2696000 | 41788000
b) | 1 X 36 W Indoor decorative T 5 Lamp s | No | 205 | 700 | 210 | 143500 | 43050 | 186550
c) | 40W LED Recess mounted 2 ' x 2' Light Fixture | No | 318 | 2180 | 150 | 693240 | 47700 | 740940
d) | 12/15W LED Surface/Recess mounted light fixture | No | 708 | 830 | 100 | 587640 | 70800 | 658440
e) | 48” (1200 mm ) ceiling fan (Bajaj excel) | Each | 323 | 2180 | 200 | 704140 | 64600 | 768740
f) | 305 mm Heavy duty exhaust fan (Bajaj fresh air fan) | Each | 120 | 2600 | 250 | 312000 | 30000 | 342000
g) | 450 mm Heavy duty, Industrial type exhaust fan with bird shutter | Each | 30 | 4200 | 350 | 126000 | 10500 | 136500
h) | 40W LED Weather Proof Street Light with 40 mm Dia Class C GI Pipe support with clamps | Each | 252 | 2500 | 600 | 630000 | 151200 | 781200
VI | L.T.CABLES
1 | Supply,Laying, Testing and commissioning of 1.1 KV grade XLPE insulated armoured alluminium conductor cable of the following size including laying and excavation and back filling and sand cushioning on top and bottom 150 mm including brick protection , on already laid cable trays, on wall including clamping etc., as per IS 7098 - Part 1 - 1983
a) | 3.5 c x 400 Sqmm A2XFY | Rmt | 32000 | 1793.836 | 150 | 57402752 | 4800000 | 62202752 | 1382 | 138.2 | 1520.2 | 273.636 | 1793.836
b) | 3.5 c x 300 Sqmm A2XFY | Rmt | 2200 | 1516.064 | 150 | 3335340.8 | 330000 | 3665340.8
c) | 3.5 c x 240 Sqmm A2XFY | Rmt | 500 | 1239.59 | 150 | 619795 | 75000 | 694795
d) | 3.5 c x 150 Sqmm A2XFY | Rmt | 800 | 763.224 | 130 | 610579.2 | 104000 | 714579.2
e) | 3.5 c x 120 Sqmm A2XFY | Rmt | 800 | 650.298 | 125 | 520238.4 | 100000 | 620238.4
f) | 3.5 c x 70 Sqmm A2XFY | Rmt | 14300 | 423.148 | 100 | 6051016.4 | 1430000 | 7481016.4
g) | 3.5 c x 35 Sqmm A2XFY | Rmt | 6600 | 233.64 | 75 | 1542024 | 495000 | 2037024
h) | 3.5 c x 25 Sqmm A2XFY | Rmt | 6400 | 189.508 | 75 | 1212851.2 | 480000 | 1692851.2
2) | Termination of the following cables with single compression cable glands and also with suitable size alluminiumn lugs including supply and fixing of Lugs.
a) | 3.5 c x 400 Sqmm | Nos | 320 | 1500 | 400 | 480000 | 128000 | 608000
b) | 3.5 c x 300 Sqmm | Nos | 54 | 1200 | 400 | 64800 | 21600 | 86400
c) | 3.5 c x 240 Sqmm | Nos | 6 | 1000 | 400 | 6000 | 2400 | 8400
d) | 3.5 c x 150 Sqmm | Nos | 6 | 800 | 400 | 4800 | 2400 | 7200
e) | 3.5 c x 120 Sqmm | Nos | 6 | 700 | 350 | 4200 | 2100 | 6300
f) | 3.5 c x 70 Sqmm | Nos | 142 | 600 | 200 | 85200 | 28400 | 113600
g) | 3.5 c x 35 Sqmm | Nos | 66 | 500 | 100 | 33000 | 6600 | 39600
h) | 3.5 c x 25 Sqmm | Nos | 64 | 400 | 100 | 25600 | 6400 | 32000
VII | SUBHEAD V : LIFTS
L-1 | Supply,Erection ,Testing and commissioning of gearless, machine roomless, passenger lifts suitable for the following persons of speed 1.75Mtr./Sec, suitable for the following floors above 60 mts approx with 3 phase VVVF motor of suitable HP to be operated on 415V+5%, 3phase 50 cycles V3F drive bARD devise and Anti-vandel design with size ... mm car made of stainlesss steel car panels with GEC/Crompton make heavyduty cabin fan and LED lights,emergency light, PVC flooring , car entrance ............ mm high protected by automatically operated gates including landing entrances,frames etc.,and simplex down collective control with or without attendant with call register, telltale indicators on all floors,car position indicator on all floors complete. (Car made up of stainless steel car panels, landing door, car door and ceiling)
ADMIN OFFICE
a) | 340KGS/5 PASSENGERS - 6 STOPS /6OPENINGS - SPEED 1.5 MPS- ACVVVF, 340kGS | Nos | 2 |  | 2000000 |  | 4000000 | 4000000
b) | 1632KGS/24 PASSENGERS - 6 STOPS /6OPENINGS - SPEED 1.5 MPS- ACVVVF, 1632kGS | Nos | 1 |  | 3000000 |  | 3000000 | 3000000
SATFF QUARTERS
a) | 340KGS/5 PASSENGERS - 4 STOPS /4OPENINGS - SPEED 1.25 MPS- ACVVVF, 340kGS | Nos | 1 |  | 2200000 |  | 2200000 | 2200000
VIII | ADMIN UPS
UPS-1 | Supply and fixing of 2 Nos of 6/16A, 5Pin Socket outlet with 2Nos of switch of 16A rating including Modular G.I Box, Front Plate and also including all fixing accessories etc complete. ( For UPS Socket) | Nos | 400 |  | 1888 |  | 755200 | 755200
UPS-2 | Providing and fixing following rating and breaking capacity and pole MCCB with thermomagnetic release and terminal spreaders in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required
a) | 125 A, 16 KA,TPMCCB | Each | 2 |  | 10030 |  | 20060 | 20060
UPS-3 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 V, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 A tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBs (but without MCBs and incomer ) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.)
a) | 12 way (4 + 12), Double door | Each | 1 |  | 25000 |  | 25000 | 25000
UPS-4 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator).
a) | 6 way (4 + 12), Double door | Each | 8 |  | 7500 |  | 60000 | 60000
UPS-5 | Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a) | 63 A | Each | 16 |  | 7500 |  | 120000 | 120000
UPS-6 | Supplying and fixing of 6A to 32A rating 240/415V, 10kA, C Curve miniature circuit breaker suitable for inductive load of following polesin the existing MCB DB complete with connections, testing and commissioning etc complete.
a) | Single Pole | Nos | 288 |  | 250 |  | 72000 | 72000
UPS-7 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required.
a) | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | RMT | 20000 |  | 236 |  | 4720000 | 4720000
b) | 4 X 10 sq. mm + 2 X 6 sq. mm earth wire | RMT | 1200 |  | 708 |  | 849600 | 849600
c) | 4 X 16 sq. mm + 2 X 6 sq. mm earth wire | RMT | 1200 |  | 944 |  | 1132800 | 1132800
UPS-8 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required including excavation in all types of soil. | Set | 10 |  | 10000 |  | 100000 | 100000
UPS-9 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets(Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm | RMT | 800 |  | 944 |  | 755200 | 755200
IX | EXTERNAL ELECTRICALS
1 | Supply,Erection,Testing and commissioning of 6 Pole Structure of 9.1Mtrs Height with 150 mm x150mm H BEAM suitable for mounting 33kV String Insulators, Isolators, and mounted on String Insulators, Isolators, and mounted on | Nos | 6 |  | 35400 |  | 212400 | 212400
2 | Supply,Fabrication ,Installation of Strutural Steel like ISMC Channels ISA Angles including welding,cutting,Two coats of primer and two coats of enamel paint including necessary hardware like nuts and bolts etc complete. | Kgs | 4000 |  | 90 |  | 360000 | 360000
3 | Supply and Erection of 33KV PCVCB. | Nos | 2 |  | 414500 |  | 829000 | 829000
4 | Supply and Erection of Metering CT's(As per Standards) | Nos | 3 |  | 41300 |  | 123900 | 123900
5 | Supply and Erection of Metering PT's(As per Standards) | Nos | 3 |  | 41300 |  | 123900 | 123900
6 | Supply and Erection of Protection CT's(As per Standards) | Nos | 3 |  | 41300 |  | 123900 | 123900
7 | Supply and Erection of 800A 33KV AB Switches | Nos | 3 |  | 45000 |  | 135000 | 135000
8 | Supply and Erection of 33KV LAS | Nos | 3 |  | 9000 |  | 27000 | 27000
9 | Supply and Erection of Panther Conductor | Rmt | 100 |  | 300 |  | 30000 | 30000
10 | Supply and Erection of 33KV Post top Insulator's | Nos | 6 |  | 500 |  | 3000 | 3000
11 | Supply and Erection of PT Clamps | Nos | 12 |  | 300 |  | 3600 | 3600
12 | Supply and Erection of VCB Clamps | Nos | 11 |  | 400 |  | 4400 | 4400
13 | Supply and Erection of 24V DC battery charger | Nos | 1 |  | 200000 |  | 200000 | 200000
14 | Supply and Erection of 33KV HT Metering Box | Nos | 1 |  | 50000 |  | 50000 | 50000
15 | Supply and Erection of 1" GI Pipe | Rmt | 100 |  | 800 |  | 80000 | 80000
16 | Supply and Erection of 4Cx2.5 sqmm CU FLEX Cable) | Rmt | 801 |  | 250 |  | 200250 | 200250
17 | Supply and Erection of 4cX2.5 sqmm Cable End Terminations Lugs | Nos | 30 |  | 236 |  | 7080 | 7080
18 | supply& erection of 33kv disc with metal parts | Nos | 6 |  | 2950 |  | 17700 | 17700
19 | 33kv Indoor Switchgear Panel with one Incomer and Four outgoing Feeder | Nos | 2 | 6468500 | 98500 | 12937000 | 197000 | 13134000
Supply,Installation,Testing and commissioning of 33 kv Rated Swthchgear Unit in Metal Enclosure fabricated out of 14 swg sheet steel and the panel to be dust and vermin proof with a degree of protection of IP 55 as per IS 3427 - 1997.The panel is to be compartmetalised with individual compartments for Bus bars, Cable and CTs and Instrument and relay control Panel. Note : CT Should be 0.2S
33kV, 1250A, 25kA breaking capacity for 1 Sec. Incomer and also with motor operated spring charged type VCB's coupled through Bus Bar of 1250A copper Bus Bar.
CONSTRUCTION - The Switch Gear Panel shall be compartmentalised Designed with cubicles frabicated out of High Quality Sheet Steel and the panels shall be dust and vermin proof and with degree of protection IP 55 as per IS 3427 -1997 . The panels shall be designed having the Following Segregations separately.
a) Busbar compartment
b) Cable and CT compartment
c)) Instrument and Relay Compartment
The clearances between phase to phase and phase to earth shall be provided in accordance with the relevant standards. The bus bars shall be supported by bus support insulators placed at regular intervals.
The panels shall be powder coated with epoxy base paint to give an aesthetically pleasing appearance. The paint shade shall be as per the requirement.
SAFETY FEATURES:
a) Mechanical Interlock and earth switch for Incomer and out goings
b) Door interlock in service position.
INCOMING VCB PANEL
33 , KV, 1250A, 25 KA for 1 sec Horizontal Draw out type Vaccum Circuit breaker with motor/manual spring charge mechanism and also with mechanical indications for breaker on /off/trip indications and also with Local Remote selector switch and with breaker TNC Switch.
CURRENT TRANSFORMER: (3 No’s) Cast Resin
Ratio 100-50 - 5/5 A - 5 A, Core 1: 15 VA, CI – 0.2S for Metering and 5P10 for protection.
POTENTIAL TRANSFORMER : (3 No’s) Cast Resin
Ratio 33000 V/ rt 3 / 110 v / rt 3 , 100 VA, CI – 0.2 for Metering and 3 P for Protection and also with 2 numbers of Under Volage relays.
METERING: ( 1set)
96 Sq.mm Digital Ammeter with selector switch Digital type
96 Sq.mm Digital Voltmeter with selector switch Digital voltmeter
Digital Multi function Meter for KW,KWH,KVA, KVAR , COS PHI Parameters reading.
INDICATION LAMPS:
1) TCH, Battery failure , Spring charge, discharge, ON, OFF and Trip Indication Lamps, Phase indication Lamps for RYB. - (1 set)
CONTROL SWITCHES/PUSH BUTTON
Bus Bar with 1250 Amps Alluminium - (1 set)
COMMON FOR SWITCHGEAR:
Heater ON and OFF Switch with Space heater, single Phase switch socket and cubicle lamp for panel illumination, MCB's for AC/DC Control - (1 set)
MS sheet enclosure suitable for outdoor installation with incoming and outgoing cable entry. - (1 set)
OUTGOING VCB - 4 nos
33 , KV, 630 A, 25 KA for 1 Sec Horizontal Draw out type Vaccum Circuit breaker with motor/manual spring charge mechanism and also with mechanical indications for breaker on /off/trip indications and also with Local Remote selector switch and with breaker TNC Switch.
CURRENT TRANSFORMER: (3 No’s)
Ratio 50 - 5/5 A - 5 A, Core 1: 15 VA, CI – 0.2S for Metering and 5P15 for protection.
METERING: ( 1set)
96 Sq.mm Digital Ammeter with selector switch Digital type
Digital Multi function Meter for KW,KWH,KVA, KVAR , COS PHI Parameters reading.
INDICATION LAMPS:
1) TCH, Battery failure , Spring charge, discharge, ON, OFF and Trip Indication Lamps, Phase indication Lamps for RYB. - (1 set)
CONTROL SWITCHES/PUSH BUTTON
Bus Bar with 1250 Amps Copper - (1 set)
COMMON FOR SWITCHGEAR:
Heater ON and OFF Switch with Space heater, single Phase switch socket and cubicle lamp for panel illumination, MCB's for AC/DC Control - (1 set)
Powerpack for Breaker Closing and Tripping coil and also for Indication Lamps, For Relays - 1 No
Relays Incomer ; Undervoltage relays 2 nos,IDMT relay ,TCH and Master trip relay.
Relays Outgoing ; IDMT relay ,TCH and Master trip relay and also with Transformer auxilary Relays and also with 12 window annunciator
33 KV INDOOR SINGLE VCB PANEL
20 | Supplying,Installing, testing and commisioning of indoor type floor mounted metal clad , 33 kv VCB panel with 3 nos vcbs ,totally enclosed and fully interlocked ,horizontal draw out, and having single breeak trip free mechanism, spring charge motor with electrical and manual charging and auto/manual closing and tripping mech anism for use in 33 kv, 3 Phase ,50 Hz, A.C. System with short circuit current level of 26.2 kA complete with self contained fully interlocked rack in and rack out mechanism , air insulated but encapsulated copper bus bars 800 amps capacity with necessary shrouds at joints with mechanical on/off indicator hand trip device ,spring release coil,shunt trip coil and also with auxiliary switch conbtacts with the following Incomer and out goings.Also the inconer should be suitable for terminating 3 c x 240 sqmm ,33 kv ( E ) , XLPE inbsulated alluminium conductor , screened cable.Out goind 3c x 150 Sqmm
a) | INCOMING VCB PANEL | SET | 3 | 1248500 | 26500 | 3745500 | 79500 | 3825000
33 , KV, 630A, 26.1 KA, Horizontal Draw out type Vaccum Circuit breaker with motor/manual spring charge mechanism and also with mechanical indications for breaker on /off/trip indications and also with Local Remote selector switch and with breaker TNC Switch.
CURRENT TRANSFORMER: (3 No’s)
Set of Dual Core dual ratio CTS 75 – 50 - 5/ - 5 A, Core 1: 15 VA, CI – 0.5for Metering and 5 P 10 for protection.
POTENTIAL TRANSFORMER: (3 No’s)
Ratio 33000 V/ rt 3 / 110 v / rt 3 , 100 VA, CI – 0.2 for Metering and 3 P for Protection and also with 2 numbers of Under Volage relays.
METERING: ( 1set)
96 Sq.mm Digital Ammeter with selector switch Digital type 0-100A.
96 Sq.mm Digital Voltmeter with selector switch Digital voltmeter 0-36KV.
Digital Multi function Meter for KW,KWH,KVA, KVAR , COS PHI Parameters reading.
INDICATION LAMPS:
1) ON, OFF and Trip Indication Lamps for RYB. - (1 set)
CONTROL SWITCHES/PUSH BUTTON
Bus Bar with 800 Amps Copper . - (1 set)
protection
Micro processor based over current , earth fault and short circuit protection.Also instantaneous short circuit protection.
The Panel shall have provision for future expansion for one VCB.
33 KV Indoor panel Incomer
UV Relays
Numeric IDMT , o/c, s/c, e/f Relay
TCH Relay, Master trip Relay
Busbars are to be provided with heat shrinks and shrouds for joinbts.
21 | Supply,Laying, Testing and commissioning of HT, 33 KV 3C X 300sqmm-grade XLPE insulated armoured alluminium conductor cable of the following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc and also including laying in already laid cable trays, on wall including clamping etc., as per IS 7098 - Part 1 - 1983 | RMT | 7000 |  | 1888 |  | 13216000 | 13216000
22 | Supply and fixing of Termination kit of 33kv , 3C X 300Sq.mm XLPE cable Termination Kit (Indoor type) | Nos | 8 |  | 59000 |  | 472000 | 472000
23 | Supply and fixing of Termination kit of 33kv , 3C X 300Sq.mm XLPE cable Termination Kit (OUTDoor type) | Nos | 20 |  | 64900 |  | 1298000 | 1298000
24 | Supply and fixing of Outdoor heat shrinkable straight through joint kit of 33kv , 3C X 300Sq.mm XLPE cable armoured alluminium conductor cable (OUTDoor type) | Nos | 24 |  | 45000 |  | 1080000 | 1080000
X | TRANSFORMERS
25 | Supply, Installation, Testing and commissioning of 2000 KVA , 33kv / 433 v, 3 PHASE, 50 Hz, Dyn 11 OUTDOOR ONAN Transformer with on load tap changer, RTCC Panel and HT Side marshalling box for termination of 33 kv grade , 3 c x 300 sqmm XLPE insulated armoured alluminium conductor screeened cable and LT side provision for connecting sandwich type of Alluminium bus trunking system of 3200 A capacity as per IS 1180 ( Level 2 ) with radiators etc | Nos | 6 | 4685800 | 52000 | 28114800 | 312000 | 28426800
26 | Supply, Installation, Testing and commissioning of 500 KVA , 33kv / 433 v, 3 PHASE, 50 Hz, Dyn 11 OUTDOOR ONAN Transformer with off load tap changer, HT Side marshalling box for termination of 33 kv grade , 3 c x 300 sqmm XLPE insulated armoured alluminium conductor screeened cable and LT side 3.5c x240 sqmm xlpe insulated armoured alluminium conductor cable | Nos | 1 | 1665000 | 22500 | 1665000 | 22500 | 1687500
27 | Supply, Installation, Testing and commissioning of 415 V, 50 Hz, A.C, 3200 A, 70ka Three phase and neutral Sandwhich type Alluminium bus bars Bus trunking system with necessary fixing Clamps and Jointing accessories including all required horizontal and vertical bends, tees for In door Application - IP -55 ( Transformer feeder Incomer ) with suitable earthing strips copper/GI on both sides .As per IS ; 8623 Part 1 & 2 (for Indoor installation-Including canopy) | Rmt | 80 |  | 46000 |  | 3680000 | 3680000
28 | Horizontal Elbow , 3200 A | NOS | 3 |  | 20000 |  | 60000 | 60000
29 | Horizontal Offset Elbow, 3200A | NOS | 3 |  | 25000 |  | 75000 | 75000
30 | Vertical Elbow , 3200 A | NOS | 3 |  | 30000 |  | 90000 | 90000
31 | Vertical Offset Elbow , 3200A | NOS | 3 |  | 35000 |  | 105000 | 105000
32 | Vertical Tee Section , 3200 A | NOS | 3 |  | 45000 |  | 135000 | 135000
33 | Flange end and BI METTALLIC Copper flexibles for connecting to bus bars at panel side and transformer side ( R,Y,B,N ONE SET ) | Nos | 6 |  | 120000 |  | 720000 | 720000
X1 | M.V PANELs
34 | MAIN PANEL - INDOOR | Nos | 3 | 7123500 | 55000 | 21370500 | 165000 | 21535500
Incomer- – 1nos (consists of)
415V, 3200A, 70KA, 4P, EDO ACB with (O/C+S/C+E/F+SPP Releases) with all protections & Microw process based releases and all other accessorizes
6A SP MCB – 3Nos
LED Type Phase Indicating Lamps (R,Y,B) – 1set
3200A/5A, Cl.0.2S , 15VA Tape wound Cts – 4Nos
0-3200A Digital type Ammeter with selector switch – 1set
0-500V Digital type voltmeter with selector switch - 1set
Load Manager – 1no
Incomer- – 2 (consists of)
415V, 3200A, 70KA, 4P, EDO ACB with (O/C+S/C+E/F+SPP Releases) with all protections & Microw process based releases and all other accessorizes
6A SP MCB – 3Nos
LED Type Phase Indicating Lamps (R,Y,B) – 1set
3200A/5A, Cl.0.2S , 15VA Tape wound Cts – 4Nos
0-3200A Digital type Ammeter with selector switch – 1set
0-500V Digital type voltmeter with selector switch - 1set
Load Manager – 1no
Incomer- – 3
(consists of)
415V, 3200A, 70KA, 4P, EDO ACB with (O/C+S/C+E/F+SPP Releases) with all protections & Microw process based releases and all other accessorizes
6A SP MCB – 3Nos
LED Type Phase Indicating Lamps (R,Y,B) – 1set
3200A/5A, Cl.0.2S , 15VA Tape wound Cts – 4Nos
0-3200A Digital type Ammeter with selector switch – 1set
0-500V Digital type voltmeter with selector switch - 1set
Load Manager – 1no
Incomer- – 4 (consists of)
415V, 3200A, 70KA, 4P, EDO ACB with (O/C+S/C+E/F+SPP Releases) with all protections & Microw process based releases and all other accessorizes
6A SP MCB – 3Nos
LED Type Phase Indicating Lamps (R,Y,B) – 1set
3200A/5A, Cl.0.2S , 15VA Tape wound Cts – 4Nos
0-3200A Digital type Ammeter with selector switch – 1set
0-500V Digital type voltmeter with selector switch - 1set
Load Manager – 1no
Bus couplers - 3 Nos (consists of)
415V, 3200A, 70KA, 4P, EDO ACB with (O/C+S/C+E/F+SPP Releases) with all protections & Microw process based releases and all other accessorizes
Note : CT should be 0.2S
Outgoing Feeders
i) 1250A,- 6No
(Each feeder consisting of)
415V, 1250A, 50KA TPN, EDO ACB with (O/C+S/C+E/F+SPP Releases) with all protections & Microw process based releases and all other accessorizes
ii) 1000A,- 2No
(Each feeder consisting of)
415V, 1000A, 50KA TPN, EDO ACB with (O/C+S/C+E/F+SPP Releases) with all protections & Microw process based releases and all other accessorizes
iii) 630A - 2Nos
(Each feeder consisting of)
415V, 630A, 50KA, TPN, MCCB with (O/C+S/C+E/F+SPP Releases) with all protections & thermal based releases and all other accessories-1No
iv) 400A - 2Nos
(Each feeder consisting of)
415V, 400A, 50KA, TPN, MCCB with (O/C+S/C+E/F+SPP Releases) with all protections & thermal based releases and all other accessories-1No
v) 100A - 1Nos
(Each feeder consisting of)
415V, 100A, 25KA, TPN, MCCB with (O/C+S/C+E/F+SPP Releases) with all protections & thermal based releases and all other accessories-1No with timer and contactor and also with 5 Nos 40A, 10KA TPN MCB as outgoings.
3200A, 3Ph, 4wire, 50Hz, 70KA, ELectrical grade aluminium busbars- 1set
Note : The scope also includes Necessary control wiring for the Electrical interlocking between the Four Incomers and Buscouplers.
35 | APFC Panel (600KVAR) - Indoor | Nos | 3 | 944000 | 22500 | 2832000 | 67500 | 2899500
Incomer:
415V, 1000A, 50KA 4P, ACB with (O/C+S/C+E/F+SPP Releases) with all protections & thermal based releases and all other accessories-1No
6A, SP MCB - 3 Nos.
RYB indicating lamps - 1 set
Voltmeter (0-500V) with selector switch - 1 set
Ammeter (0-1000A) with selector switch - 1 set
16 Stage APFC Relay-1No
1000A/5A, Cl.0.2S , 15VA Tape wound Cts – 3Nos
a) Outgoing Feeders
50 KVAR capacitor banks (Ducati / Asian / Mehar) - 10Nos(Each consisting of)
415V, 80A,4P ISOLATER – 1 Nos.
70A, PC contactors - 1 Nos
Push buttons – 1set
ON/OFF indicating lamps – 1set
b) 25 KVAR capacitor banks (Ducati / Asian / Mehar) - 4Nos(Each consisting of)
415V, 63A,4P ISOLATER – 1 Nos.
60A, PC contactors - 1 Nos
Push buttons – 1set
ON/OFF indicating lamps – 1set
1000A, 3Ph, 4wire, 50Hz, 50KA, ELectrical grade aluminium busbars- 1set
X11 | EARTHING
a) | Supply and providing earth electrode with 600 x 600 x 3.15 copper plate electrode enclosed in cement concrete chamber of size 400x 400 x 400mm and 300 x 300mm size cast iron cover with cast iron frame embedded in cement mortar to be provided on the top of the masonry chamber, use of salt, coat or coke as required for earthing media, providing 50mm diameter GI pipe with standard type GI funnel arrangement at top and all complete as per IS: 3043 - 1987 | Nos | 6 |  | 14160 |  | 84960 | 84960
b) | Suppy,Installation of 40 mm dia GI Earthpipe of 3 mtr length Earth Station including excavation,back filling and construction of earth chamber.The scope includes civil work like excavation,back filling and construction of chamber with cast iron cover of size 300 x 300 MM and providing charcoal, salt and sand for the earth pit as per IS 3043. | Nos | 16 |  | 5000 |  | 80000 | 80000
c) | Supply and fixing of following earth strips/ conductors. The scope includes supply and fixing of copper lugs wherever found necessary, brass bolts, nuts and washers for fixing arrangement etc., (from earth station to main panel).
i) | 75 x 5 MM G.I. Flat | Rmt | 300 |  | 472 |  | 141600 | 141600
ii) | 50 x 5 MM G.I. Flat | Rmt | 200 |  | 236 |  | 47200 | 47200
iii) | 8 SWG G.I.Wire | Rmt | 300 |  | 24 |  | 7200 | 7200
iv) | 75 x 10 MM Copper. Flat | Rmt | 300 |  | 3304 |  | 991200 | 991200
XIII | L.T.CABLES
37 | Supply,Laying, Testing and commissioning of 1.1 KV grade XLPE insulated armoured alluminium conductor cable of the following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc and also including laying in already laid cable trays, on wall including clamping etc., as per IS 7098 - Part 1 - 1983
a) | 3.5 c x 300 Sqmm A2XFY | Rmt | 500 |  | 1770 |  | 885000 | 885000
b) | 4 c x 6 Sqmm A2XWY | Rmt | 5000 |  | 295 |  | 1475000 | 1475000
c) | Termination of the following cables with single compression cable glands and also with suitable size alluminiumn lugs including supply and fixing of Lugs.
i) | 3.5 c x 300 Sqmm | Nos | 18 |  | 1416 |  | 25488 | 25488
ii) | 4 c x 6 Sqmm | Nos | 500 |  | 236 |  | 118000 | 118000
Control Cables
c) | Supply,Laying, Testing and commissioning of 1.1 KV grade XLPE/PVC insulated armoured copper conductor control cable of the following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc and also including laying in already laid cable trays, on wall including clamping etc., as per IS 7098 - Part 1 - 1983
i) | 4c x 2.5 Sqmm | Rmt | 400 | 250 | 30 | 100000 | 12000 | 112000
ii) | 7c x 2.5 Sqmm | Rmt | 400 | 400 | 55 | 160000 | 22000 | 182000
iii) | 12c x 2.5 Sqmm | Rmt | 400 | 670 | 95 | 268000 | 38000 | 306000
iv) | 19c x 2.5 Sqmm | Rmt | 400 | 1025 | 140 | 410000 | 56000 | 466000
d) | Termination of the following cables with single compression cable glands and also with suitable size alluminiumn lugs including supply and fixing of Lugs.
i) | 4c x 2.5 Sqmm | Nos | 6 | 180 | 90 | 1080 | 540 | 1620
ii) | 7c x 2.5 Sqmm | Nos | 6 | 250 | 110 | 1500 | 660 | 2160
iii) | 12c x 2.5 Sqmm | Nos | 6 | 380 | 180 | 2280 | 1080 | 3360
iv) | 19c x 2.5 Sqmm | Nos | 4 | 550 | 260 | 2200 | 1040 | 3240
39 | SAFETY ITEMS
Supply, Intallation, Testing and commissioning of the Follwing Safety and Fire fighting Systems as per standrads and specification
a) | Fire Extinguishers - 5 KG CAPACITY CO 2 Confirming to IS 2878 fitted with discharge bend pipe and horn | NOS | 6 |  | 5900 |  | 35400 | 35400
b) | Sand Bucket with stand with 4 Nos of buckets on top and bottom | SET | 3 |  | 2000 |  | 6000 | 6000
c) | 415 V Danger Boards | NOS | 12 |  | 250 |  | 3000 | 3000
d) | 33 KV Hand Gloves | Pair | 3 |  | 300 |  | 900 | 900
e) | 33 KV Danger Boards | NOS | 4 |  | 200 |  | 800 | 800
f) | Supply,Fixing of 4.5 kg co2 fire extinguishers with necessary fixing Clamps | NOS | 4 |  | 5200 | 100 | 20800 | 20700
g) | 33 KV Rubber Mats | NOS | 12 |  | 4500 | 150 | 54000 | 53850
h) | 415 V Rubber Mats | NOS | 30 |  | 3200 | 150 | 96000 | 95850
XIV | STREET LIGHTING
STREET LIGHTING POLES
1 | Supply and erection of steel stepped and swaged tubular poles of 9 mtr long (410 SP25 )(1.5 mtr below ground ) with base plate earthing studs 1.5 mtr out reach Double arm , FRP terminal Box 2 Nos of 40 mm Dia Class B G.I Pipe ,0.5 mtr Long for incoming and outgoing cables including excavation in all types of soil ,PCC 1:2:4 ,PCC Pedestal with painting with black bitumen paint inside the coping for embedded portion and two coats of Zinc chromite primer and two coats of Alluminium paint externally for length above the ground.The pole shall be with FRP junction box consisting of 10A MCB.The wiring from Junction box to Light fixture shall be carried out with 3 Core 2.5 Sqmm Copper conductor flexible cable. The streetLight Pole shall be fixed with 70W LED street Light fixture including supply of controlgear / driver and lamp(Make : Cat No.LR02-102-XXX-57-G2 ,WIPRO MAKE / CAT NO - Greenline V2 (BRP410) Philips make. ) - 2 Nos | Nos | 40 | 23500 | 5500 | 940000 | 220000 | 1160000
2 | Supply and erection of steel stepped and swaged tubular poles of 9 mtr long (410 SP25 )(1.5 mtr below ground ) with base plate earthing studs 1.5 mtr out reach single arm , FRP terminal Box 2 Nos of 40 mm Dia Class B G.I Pipe ,0.5 mtr Long for incoming and outgoing cables including excavation in all types of soil ,PCC 1:2:4 ,PCC Pedestal with painting with black bitumen paint inside the coping for embedded portion and two coats of Zinc chromite primer and two coats of Alluminium paint externally for length above the ground.The pole shall be with FRP junction box consisting of 10A MCB.The wiring from Junction box to Light fixture shall be carried out with 3 Core 2.5 Sqmm Copper conductor flexible cable. The cable shall be fixed with 70W LED street Light fixture including supply of controlgear / driver and lamp(Make : Cat No.LR02-102-XXX-57-G2 ,WIPRO MAKE / CAT NO - Greenline V2 (BRP410) Philips make. ) | Nos | 340 | 22500 | 5500 | 7650000 | 1870000 | 9520000
3 | Supply, fixing, testing and commissioning of 5.0mts long, 65mm dia GI pole including labour charges for erection of tubular poles with base plate coil earthing, concreting, coping and painting of the pole with one coat of redoxide paint and two coats of aluminium paint including cost of conveyance of all materials to site etc.,including 40 W LED STREET LIGHT equilent model of PHILIPS make (Model No.BRP 040/40 W with necessary civil works like foundation for the Poles, pillar boxes, digging trenching etc for street lighting Poles.The Pole shall be supplied with FRP Junction Box and 2 Nos of 50 mm Dia Class B G.I Pipe and also wiring from Junction box to Light fixture shall be carried out with 3 Core 2.5 Sqmm Copper conductor flexible cable. | Nos | 30 | 15000 | 4000 | 450000 | 120000 | 570000
Cabling
4 | Supplying and laying,Testing and commissioning of XLPE insulated armoured alluminium conductor cable 1100 V grade with ISI mark following stranded/ solid, aluminium conductor complete by making Burried in soil upto 0.6M deep embeeding the cable complete with sand bed . Thick layers and bricks/stones placed on top of the cable width wise all over the run and back filling the excavated earth without stones are hard materials and making the surface proper providing route indicators etc., complete (Makes : POLYCAB,HAVELLS,UNIVERSAL)
a) | 4C x 10 Sqmm | Rmt | 7000 | 200 | 75 | 1400000 | 525000 | 1925000
b) | Termination of the following cables with single compression weather proof cable glands and also with suitable size alluminiumn lugs including supply and fixing of Lugs.
i) | 4C x 10 Sqmm | Nos | 760 | 350 | 180 | 266000 | 136800 | 402800
5 | Providing Spiral Coil earthing using 8 SWG GI wire buried to a depth of 1500mm including excavation , refilling, spreading of salt and charcoal as per drawing and connection GI wire to pole using GI bolt and nut complete as required. Cost including all labour rates and overheads & profits etc., complete. | Nos | 210 | 2250 | 650 | 472500 | 136500 | 609000
DG SETS
1 | Supply,Installation,Testing and commissioning of 1010 KVA ,415 Volts at 1500 RPM,0.8 lagging Power factorat 415 V suitable for 50Hz ,3 Phase system and for 0.85 Load factor and consisting the followings. including D.G.Set with Accoustic Enclosure and with diesel tank of capacity 990 Ltrs and also with Suitable size Power and Control panel with ACB and necessary control wiring. | Nos | 3 |  | 7250000 |  | 21750000 | 21750000
2 | Supply, Installation, Testing and commissioning of 415 V, 50 Hz, A.C, 1600 A, 70ka Three phase and neutral Sandwhich type Alluminium bus bars Bus trunking system with necessary fixing Clamps and Jointing accessories including all required horizontal and vertical bends, tees for In door Application - IP -55 ( Transformer feeder Incomer ) with suitable earthing strips copper/GI on both sides .As per IS ; 8623 Part 1 & 2 (for Indoor installation-Including canopy) | Rmt | 50 |  | 44840 |  | 2242000 | 2242000
3 | Horizontal Elbow , 1600 A | NOS | 3 |  | 23600 |  | 70800 | 70800
4 | Horizontal Offset Elbow, 1600A | NOS | 3 |  | 29500 |  | 88500 | 88500
5 | Vertical Elbow , 1600 A | NOS | 3 |  | 33040 |  | 99120 | 99120
6 | Vertical Offset Elbow , 1600A | NOS | 3 |  | 33040 |  | 99120 | 99120
7 | Vertical Tee Section , 1600 A | NOS | 3 |  | 33040 |  | 99120 | 99120
8 | Flange end and BI METTALLIC Copper flexibles for connecting to bus bars at panel side and transformer side ( R,Y,B,N ONE SET ) | Nos | 6 |  | 100000 |  | 600000 | 600000
9 | EARTHING
a) | Supply and providing earth electrode with 600 x 600 x 3.15 copper plate electrode enclosed in cement concrete chamber of size 400x 400 x 400mm and 300 x 300mm size cast iron cover with cast iron frame embedded in cement mortar to be provided on the top of the masonry chamber, use of salt, coat or coke as required for earthing media, providing 50mm diameter GI pipe with standard type GI funnel arrangement at top and all complete as per IS: 3043 - 1987 | Nos | 6 |  | 12000 |  | 72000 | 72000
b) | Suppy,Installation of 40 mm dia GI Earthpipe of 3 mtr length Earth Station including excavation,back filling and construction of earth chamber.The scope includes civil work like excavation,back filling and construction of chamber with cast iron cover of size 300 x 300 MM and providing charcoal, salt and sand for the earth pit as per IS 3043. | Nos | 8 |  | 5000 |  | 40000 | 40000
c) | Supply and fixing of following earth strips/ conductors. The scope includes supply and fixing of copper lugs wherever found necessary, brass bolts, nuts and washers for fixing arrangement etc., (from earth station to main panel).
i) | 75 x 5 MM G.I. Flat | Rmt | 300 |  | 472 |  | 141600 | 141600
ii) | 50 x 5 MM G.I. Flat | Rmt | 200 |  | 236 |  | 47200 | 47200
iii) | 8 SWG G.I.Wire | Rmt | 300 |  | 24 |  | 7200 | 7200
iv) | 75 x 10 MM Copper. Flat | Rmt | 300 |  | 3304 |  | 991200 | 991200
L.T.CABLES
10 | Supply,Laying, Testing and commissioning of 1.1 KV grade XLPE insulated armoured alluminium conductor cable of the following size including laying and excavation and back filling and sand cushioning on top and bottom 150 mm including brick protection , on already laid cable trays, on wall including clamping etc., as per IS 7098 - Part 1 - 1983
a) | 3.5 c x 400 Sqmm A2XFY | Rmt | 12000 | 2760 | 380 | 33120000 | 4560000 | 37680000
2) | Termination of the following cables with single compression cable glands and also with suitable size alluminiumn lugs including supply and fixing of Lugs.
a) | 3.5 c x 400 Sqmm | Nos | 30 | 2150 | 650 | 64500 | 19500 | 84000
[7 empty] | T0TAL | 414535691
12 | Solar power sytem (2000kwp) | [6 empty] | 80000000
13 | Telephone Lan conduits | [6 empty] | 7000000
14 | CCTV System | [6 empty] | 18000000
15 | High Mast Lighting | [6 empty] | 15000000
16 | PEB Shed Earthing | [6 empty] | 5000000
17 | COMPRESSED AIR SYSTEM | [6 empty] | 44100000
18 | DG SET STACK EXHAUST SYSTEM | [6 empty] | 2500000
19 | CEIG Approval | [6 empty] | 500000
[7 empty] | G.TOTAL | 586635691